Maestro GPRS Modem and ADAM Module Configuration for Wireless Data Communication using Static IP Sim Cards

SWA AUTOMATION PVT. LTD.

C-501, PRESIDENT PLAZA,

NR. R.T.O. RING ROAD,

SURAT, GUJARAT, INDIA – 395001

1

- SYSTEM ARCHITECTURE

1

2

- GPRS Modem and ADAM Module Configuration for Wireless Data Communication

- Require Instruments

  - Maestro Modem

  - ADAM Module 4520 / RS232 to RS485 Converter

  - ADAM Module 4017+ / Analog Signal

  - ADAM Module 4051 / Digital Input

- Require Softwares For Communication

  - Maestro Configuration Software

  - Advantech Adam.NET Utility

- We Have Two GPRS Modems. In this two modems one will act as a server and other will be client.

- For starting communication or troubleshooting modem communication first ensure that your both sim

card having Internet Connection and STATIC IP at server modem.

- Now we have to set configuration data of GPRS Modem with the use of Maestro Configuration Software.

2

3

Maestro M100 3G Setup Procedure

As a Server

- Install Maestro Configuration Software

- Please start Setup.exe and follow below instruction.

- Port Select

  - Com Port : Select the Correct COM Port to Use. Selected COM Port Will Be Saved After Connection.

  - Serial Configuration : Select the Correct Setting for Serial.

Baud Rate : 9600

Formate : 8 data 1 stop

Parity : None

  - After Setting this Configuration Connect Modem. Once Modem is connected then Switch to Modem Status.

3

4

- Modem Status :

- Network Information : It Shows the Received Signal Strength, SIM Card Status, SIM Card Name. You can see the IP address and IP Connection in below image. If IP address is displays and IP Connection=1,1 then It Means your Modem is Connected with internet.

- Actions : If IP is not display then you can press either IP Connect Button or Reboot Modem for Refresh.

4

5

- Serial Port :

- Band Selector : Select “auto-band Mode” and Save Band Selection.

- Serial Port : Select the Correct Setting for Serial.

Baud Rate : 9600

Formate : 8 data 1 stop

Parity : None

- Save Serial Port Settings.

5

6

- Data & Serial to IP Socket :

- Data Access : Fill the APN of  BSNL which you used in Modem.

  - BSNL : bsnlstatic ( for static IP)

- Serial to TCP : IP: 255.255.255.255

Port : Define port for communication. At the time of communication port will open when Connection is Establish.

Connection Type : Server

- Auto Connection : Type/Enabled : TCP Buffer Delay : 2

- Save upper settings and you can see in below image.

6

7

Maestro M100 3G Setup Procedure

As a Client

 Port Select

- Com Port : Select the Correct COM Port to Use. Selected COM Port Will Be Saved After Connection.

- Serial Configuration : Select the Correct Setting for Serial.

Baud Rate : 9600

Formate : 8 data 1 stop

Parity : None

- After Set this Configuratin Connect Modem. Once Modem is connected then Switch to Modem Status.

7

8

- Modem Status :

- Network Information : It Shows the Received Signal Strength, SIM Card Status, SIM Card Name. You can see in below image that IP address doesn’t show and IP Connection=1,0 that means either your Modem can’t connected with internet or you don’t have data plan in this SIM Card

- Actions : If IP is not display then you can press either IP Connect Button or Reboot Modem for Refresh.

8

9

- Serial Port :

- Band Selector : Select “auto-band Mode” and Save Band Selection.

- Serial Port : Select the Correct Setting for Serial.

Baud Rate : 9600

Formate : 8 data 1 stop

Parity : None

- Save Serial Port Settings.

9

10

 Data & Serial to IP Socket :

- Data Access : Fill the APN of Network Company which you used in Modem.

- Serial to TCP : IP: Enter the Static IP of Server Modem , you can see in below image.

Port : Define port which you open for data Communication (must be same as server modem).

Connection Type : Client

- Auto Connection : Type/Enabled : TCP Buffer Delay : 2

- Save upper settings and you can see in below image.

10

11

Advantech Adam.NET Utility  Setup Procedure

- Open Advantech Adam.NET Utility Application.

- Ensure that your ADAM-4520, ADAM-4017+ and ADAM 4520 is connected with Data(+) and Data(-) pin and ADAM-4520 is in Normal Mode.

- Check Baudrate of Adam-4520 in inside Modem. There are 10 switches to set Baud rate.

- By default baud rate is 9600. Then also you have to check and confirm.

- Connect your Adam Module (ADAM-4520) with PC/Laptop through MOXA U-Port.

- Open Advantech Adam.NET Utility and Right Click on ADAM4000_5000 in Left Pane then click on Refresh Subnode.

- You can see your COM port where you connect yout Adam Module.

- Select com port and right click on it. Then search Module from COM X.

- If your Module connected with PC/Laptop then Module will reflect on COM Port.

- Set Module Configuration. Baud Rate : 9600 Protocol : Modbus

Data Area : Define Range 4 to 20 mA

- ADAM-4017+ Hardware Setting :

- Check your Jumper inside ADAM-4017+. Which is use for 4 to 20 mA and 0 to 10V.

- Set your Jumper in 4 to 20 mA Configuration.

11