## Slide 1: Modbus and TCP Modbus Protocol
Modbus Request and Response Query

## Slide 2: Modbus Protocol
The Modbus devices communicate using a master-slave technique, in which only one device (the master) can initiate transactions(called ‘queries’). The other devices (the slaves) respond by supplying the requested data to the master, or by taking the action requested in the query.
The master can address individual slaves, or can initiate a broadcast messages to all slaves. Slaves return a message(called a ‘response’) to queries that are addressed to them individually. Responses are not returned to broadcast queries from the master.
In EMS master is a X-Force DAS Software and slave is a energy Meter

## Slide 3: Modbus Protocol
Modbus Read Request Query(8 Byte) (Holding and Input Register) |  |  |  | 
Slave Address | Function Code | Starting Address | No of register | CRC
1 Byte | 1 Byte | 2 Byte | 2 Byte | 2 Byte
1 | 3 | 3901 | 10 | 

## Slide 4: Mod Simulator

## Slide 5: Modbus Protocol
Modbus Read Response Query(5 Byte + No of Register * 2) (Holding and Input Register) |  |  |  | 
Slave Address | Function Code | Byte Count | Data=No of register * 2 | CRC
1 Byte | 1 Byte | 1 Byte | 10 Register * 2 =20 Byte | 2 Byte
1 | 3 | 20 |  | 

## Slide 6: DAS Serial Communication

## Slide 7: Modbus Protocol
Modbus Read Request Query(8 Byte) (Coil and Input Status) |  |  |  | 
Slave Address | Function Code | Starting Address | No of register | CRC
1 Byte | 1 Byte | 2 Byte | 2 Byte | 2 Byte
1 | 1 or 2 | 0001 | 10 | 

## Slide 8: Modbus Protocol
Modbus Read Response Query (5 Byte + Ceiling(No of Register /8)) (Coil and Input Status) |  |  |  | 
Slave Address | Function Code | Byte Count | Data=Ceiling(No of register / 8) Byte | CRC
1 Byte | 1 Byte | 1 Byte | 10 Register / 8 =Ceiling(1.25 Byte)=2 Byte | 2 Byte
1 | 1 or 2 | 2 | 10 bit Data (2 Byte data) | 

## Slide 9: Modbus Protocol
Modbus Single register Write Request Query for(8 Byte) (Holding and Input Register) |  |  |  | 
Slave Address | Function Code | Starting Address | Write data | CRC
1 Byte | 1 Byte | 2 Byte | 2 Byte | 2 Byte
1 | 6 | 3901 | 10 | 

## Slide 10: Modbus Protocol
Modbus Single register Write Response Query for(8 Byte) (Holding and Input Register) |  |  |  | 
Slave Address | Function Code | Starting Address | Write data | CRC
1 Byte | 1 Byte | 2 Byte | 2 Byte | 2 Byte
1 | 6 | 3901 | 10 | 

## Slide 11: Modbus Protocol
Modbus Multiple register Write Request Query for (9 Byte+ (No of Register*2) Byte) (Holding and Input Register) |  |  |  |  |  |  | 
Slave Address | Function Code | Starting Address | No Of Register | Byte Count | Data | Data | CRC
1 Byte | 1 Byte | 2 Byte | 2 Byte | 1 Byte | 2 Byte | 2 Byte | 2 Byte
1 | 16 | 3901 | 2 | 4 | 25.65 | 85.02 | 

## Slide 12: Modbus Protocol
Modbus Multiple register Write Response Query for(8 Byte) (Holding and Input Register) |  |  |  | 
Slave Address | Function Code | Starting Address | No of write Register | CRC
1 Byte | 1 Byte | 2 Byte | 2 Byte | 2 Byte
1 | 16 | 3901 | 2 | 

## Slide 13: TCP Modbus Protocol
TCP Modbus Read Request Query(12 Byte) (Holding and Input Register) |  |  |  |  |  | 
Transaction ID | Protocol ID | Length | Slave Address | Function Code | Starting Address | No of register
2 Byte | 2 Byte | 2 Byte | 1 Byte | 1 Byte | 2 Byte | 2 Byte
0-65535 | 0 | 6 | 1 | 3 | 3901 | 10

## Slide 14: TCP Modbus Protocol
TCP Modbus Read Response Query(12 Byte) (Holding and Input Register) |  |  |  |  |  | 
Transaction ID | Protocol ID | Length | Slave Address | Function Code | Byte Count | Data
2 Byte | 2 Byte | 2 Byte | 1 Byte | 1 Byte | =No of register*2 Byte | No of register * 2 Data Byte
0-65535 | 0 | 6 | 1 | 3 | =10*2=20 | 20 Byte data

## Slide 15: TCP Modbus Protocol
Other Read and Write TCP Modbus Query same as Modbus Protocol query.
Just add three parameter like Transaction ID, Protocol ID, Length and Remove CRC parameter from TCP Modbus Protocol.

## Slide 16: Kalpesh Mangukiya
Thank you 