OI ABCIP CompactLogix Configuration

Allen-Bradley Compact logix Hardware Setup

Power supply

LAN

Process

Power Supply

SMC

LAN

ABCIP

WWClient

Suitelink

The Wonderware ABCIP OI (Operations Integration) Server is a Microsoft Windows application that allows client applications direct and indirect access to Allen-Bradley families of ControlLogix, GuardLogix, FlexLogix, CompactLogix, SoftLogix 5800, MicroLogix, PLC-5, and SLC500 controllers.

The OI Server does not require any Rockwell Software RSLinx™ package

The ABCIP OI Server communicates with supported devices either directly or indirectly across the following device networks:

- ControlNet

- Data Highway 485 (DH485)

- Data Highway Plus (DH+)

- DeviceNet

- Ethernet

The ABCIP OI Server will provide direct and indirect connectivity to the following Allen-Bradley controllers:

- ControlLogix Controllers

- GuardLogix Controllers

- SoftLogix 5800 Controllers

- CompactLogix Controllers

- FlexLogix Controllers

- MicroLogix Controllers

- PLC-5 Controllers

- SLC500 Controllers

- Install ABCIP OI After installation it will show in the SMC.

- Navigate to the Operations Integration Supervisory Sensors – Allen- Bradley ABCIP and right click on the configuration and add PORT_CIP Connection

- Add ENB_CPLX Connection (For CompactLogix)

- Enter IP Address of PLC and Save it.

- Add BACKPLANE_CPLX connection

- Add Logix_CPLX Connection.

- Add Device Group and device items

- Activate OI ABCIP Server

- Open WW Client.

- Go to connection and create connection.

- Go to item and add item.

- Now tags will show in the wonderware client.

- You can also view that data in SMC in Diagnostics.

OI ABCIP ControlLogix Configuration

Allen-Bradley Control logix Hardware Setup

LAN

Process

Power Supply

SMC

LAN

ABCIP

WWClient

Suitelink

- Install ABCIP OI After installation it will show in the SMC.

- Navigate to the Operations Integration Supervisory Sensors – Allen- Bradley ABCIP and right click on the configuration and add PORT_CIP Connection

- Click on PLC and add ENB_CLX Connection

- Enter IP Address of PLC

- Right click on ENB_CLX_000 and Add Backplane_CLX Connection

- Right Click on Backplane and add Logix 5000 Connection and add device Group and device items.

7. Now open WW Client and check connectivity of tags as described above.