## IO Assignment
Sr. No. | System Cabinet No. | Node No. | Rack No | Slot No. | Chan. No. | Module Type | PLC Address | Instrument Type | Instrument-Tag- | PLC Tag | Equipment Name | Range | Unit | I/O Type | Signal Potential | Barrier | Barrier No. | Barrier TB No. |  | Cabinet Name / Number | Location (Front / Rear | TB Name | Panel TB Termioal NO |  | Cabinet Name / Number | Location (Front / Rear | JB Name | JB Terminal |  |  | Loop Drawing No
1 | SC-1 | 1 | 0 | 1 | 0 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[0].Value | Level Switch-Vibration Fork Type | EK-66-LS-6501 | EK_LS_6501_66 | Coagulant Dosing Tank | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 1 | 2 | MC-1 | FRONT | EK-66-JBA-1104 | +1 | -2 | - | OIL-400-EK-I-DW-3033 (Template-T2)
2 | SC-1 | 1 | 0 | 1 | 1 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[1].Value | Level Switch-Vibration Fork Type | EK-66-LS-6502 | EK-LS_6502_66 | PE Dosing Tank | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 3 | 4 | MC-1 | FRONT | EK-66-JBA-1104 | +3 | -4 | - | OIL-400-EK-I-DW-3033 (Template-T2)
3 | SC-1 | 1 | 0 | 1 | 2 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[2].Value | Level Switch-Vibration Fork Type | EK-66-LS-6503 | EK-LS_6503_66 | DWPE Dosing Tank | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 5 | 6 | MC-1 | FRONT | EK-66-JBA-1104 | +5 | -6 | - | OIL-400-EK-I-DW-3033 (Template-T2)
4 | SC-1 | 1 | 0 | 1 | 3 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[3].Value | Level Switch-Displacer Type | EK-66-LS-6504 | EK-LS_6504_66 | Level Switch-Displacer Type | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 7 | 8 | MC-1 | FRONT | EK-66-JBA-1104 | +7 | -8 | - | OIL-400-EK-I-DW-3033 (Template-T2)
5 | SC-1 | 1 | 0 | 1 | 4 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[4].Value | Level Switch-Displacer Type | EK-66-LS-6505 | EK-LS_6505_66 | Calrified Water Tank | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 9 | 10 | MC-1 | FRONT | EK-66-JBA-1104 | +9 | -10 | - | OIL-400-EK-I-DW-3033 (Template-T2)
6 | SC-1 | 1 | 0 | 1 | 5 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[5].Value | Level Switch-Displacer Type | EK-66-LS-6506 | EK-LS_6506_66 | Treated Water Storage Tank | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 11 | 12 | MC-1 | FRONT | EK-66-JBA-1104 | +11 | -12 | - | OIL-400-EK-I-DW-3033 (Template-T2)
7 | SC-1 | 1 | 0 | 1 | 6 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[6].Value | Level Switch-Vibration Fork Type | EK-66-LS-6507 | EK-LS_6507_66 | NaoCL Dosing Tank | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 13 | 14 | MC-1 | FRONT | EK-66-JBA-1104 | +13 | -14 | - | OIL-400-EK-I-DW-3033 (Template-T2)
8 | SC-1 | 1 | 0 | 1 | 7 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[7].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 15 | 16 | MC-1 | FRONT | EK-66-JBA-1104 | +15 | -16 | - | Spare
9 | SC-1 | 1 | 0 | 1 | 8 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[8].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 17 | 18 | MC-1 | FRONT | EK-66-JBA-1104 | +17 | -18 | - | Spare
10 | SC-1 | 1 | 0 | 1 | 9 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[9].Value | Proximity Switch | EK-66-ZSO-6516 | EK-ZSO_6516_66 | Suction of Microbubble Pump-A (EK-PBA-6509A) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-1 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1103 | 1 | 2 | MC-1 | FRONT | EK-66-JBA-1103 | +1 | -2 | - | OIL-400-EK-I-DW-3033 (Template-T1)
11 | SC-1 | 1 | 0 | 1 | 10 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[10].Value | Proximity Switch | EK-66-ZSC-6516 | EK-ZSC_6516_66 | Suction of Microbubble Pump-A (EK-PBA-6509A) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-1 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1103 | 3 | 4 | MC-1 | FRONT | EK-66-JBA-1103 | +3 | -4 | - | OIL-400-EK-I-DW-3033 (Template-T1)
12 | SC-1 | 1 | 0 | 1 | 11 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[11].Value | Proximity Switch | EK-66-ZSO-6517 | EK-ZSO_6517_66 | Suction of Microbubble Pump-B (EK-PBA-6509B) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-2 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1103 | 5 | 6 | MC-1 | FRONT | EK-66-JBA-1103 | +5 | -6 | - | OIL-400-EK-I-DW-3033 (Template-T1)
13 | SC-1 | 1 | 0 | 1 | 12 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[12].Value | Proximity Switch | EK-66-ZSC-6517 | EK-ZSC_6517_66 | Suction of Microbubble Pump-B (EK-PBA-6509B) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-2 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1103 | 7 | 8 | MC-1 | FRONT | EK-66-JBA-1103 | +7 | -8 | - | OIL-400-EK-I-DW-3033 (Template-T1)
14 | SC-1 | 1 | 0 | 1 | 13 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[13].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-13 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1103 | 9 | 10 | MC-1 | FRONT | EK-66-JBA-1103 | +9 | -10 | - | Spare
15 | SC-1 | 1 | 0 | 1 | 14 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[14].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-13 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1103 | 11 | 12 | MC-1 | FRONT | EK-66-JBA-1103 | +11 | -12 | - | Spare
16 | SC-1 | 1 | 0 | 1 | 15 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[15].Value | Proximity Switch | EK-66-ZSO-6501 | EK-ZSO_6501_66 | Inlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-3 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1101 | 1 | 2 | MC-1 | FRONT | EK-66-JBA-1101 | +1 | -2 | - | OIL-400-EK-I-DW-3033 (Template-T1)
17 | SC-1 | 1 | 0 | 1 | 16 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[16].Value | Proximity Switch | EK-66-ZSC-6501 | EK-ZSC_6501_66 | Inlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-3 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1101 | 3 | 4 | MC-1 | FRONT | EK-66-JBA-1101 | +3 | -4 | - | OIL-400-EK-I-DW-3033 (Template-T1)
18 | SC-1 | 1 | 0 | 1 | 17 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[17].Value | Proximity Switch | EK-66-ZSO-6502 | EK-ZSO_6502_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-4 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1102 | 1 | 2 | MC-1 | FRONT | EK-66-JBA-1102 | +1 | -2 | - | OIL-400-EK-I-DW-3033 (Template-T1)
19 | SC-1 | 1 | 0 | 1 | 18 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[18].Value | Proximity Switch | EK-66-ZSC-6502 | EK-ZSC_6502_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-4 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1102 | 3 | 4 | MC-1 | FRONT | EK-66-JBA-1102 | +3 | -4 | - | OIL-400-EK-I-DW-3033 (Template-T1)
20 | SC-1 | 1 | 0 | 1 | 19 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[19].Value | Proximity Switch | EK-66-ZSO-6503 | EK_ZSO_6503_66 | Inlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-5 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1101 | 5 | 6 | MC-1 | FRONT | EK-66-JBA-1101 | +5 | -6 | - | OIL-400-EK-I-DW-3033 (Template-T1)
21 | SC-1 | 1 | 0 | 1 | 20 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[20].Value | Proximity Switch | EK-66-ZSC-6503 | EK_ZSC_6503_66 | Inlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-5 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1101 | 7 | 8 | MC-1 | FRONT | EK-66-JBA-1101 | +7 | -8 | - | OIL-400-EK-I-DW-3033 (Template-T1)
22 | SC-1 | 1 | 0 | 1 | 21 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[21].Value | Proximity Switch | EK-66-ZSO-6504 | EK_ZSO_6504_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-6 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1101 | 9 | 10 | MC-1 | FRONT | EK-66-JBA-1101 | +9 | -10 | - | OIL-400-EK-I-DW-3033 (Template-T1)
23 | SC-1 | 1 | 0 | 1 | 22 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[22].Value | Proximity Switch | EK-66-ZSC-6504 | EK_ZSC_6504_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-6 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1101 | 11 | 12 | MC-1 | FRONT | EK-66-JBA-1101 | +11 | -12 | - | OIL-400-EK-I-DW-3033 (Template-T1)
24 | SC-1 | 1 | 0 | 1 | 23 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[23].Value | Proximity Switch | EK-66-ZSO-6505 | EK_ZSO_6505_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-7 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1101 | 13 | 14 | MC-1 | FRONT | EK-66-JBA-1101 | +13 | -14 | - | OIL-400-EK-I-DW-3033 (Template-T1)
25 | SC-1 | 1 | 0 | 1 | 24 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[24].Value | Proximity Switch | EK-66-ZSC-6505 | EK_ZSC_6505_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-7 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1101 | 15 | 16 | MC-1 | FRONT | EK-66-JBA-1101 | +15 | -16 | - | OIL-400-EK-I-DW-3033 (Template-T1)
26 | SC-1 | 1 | 0 | 1 | 25 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[25].Value | Proximity Switch | EK-66-ZSO-6506 | EK_ZSO_6506_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-8 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1102 | 5 | 6 | MC-1 | FRONT | EK-66-JBA-1102 | +5 | -6 | - | OIL-400-EK-I-DW-3033 (Template-T1)
27 | SC-1 | 1 | 0 | 1 | 26 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[26].Value | Proximity Switch | EK-66-ZSC-6506 | EK_ZSC_6506_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-8 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1102 | 7 | 8 | MC-1 | FRONT | EK-66-JBA-1102 | +7 | -8 | - | OIL-400-EK-I-DW-3033 (Template-T1)
28 | SC-1 | 1 | 0 | 1 | 27 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[27].Value | Proximity Switch | EK-66-ZSO-6507 | EK_ZSO_6507_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-9 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1102 | 9 | 10 | MC-1 | FRONT | EK-66-JBA-1102 | +9 | -10 | - | OIL-400-EK-I-DW-3033 (Template-T1)
29 | SC-1 | 1 | 0 | 1 | 28 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[28].Value | Proximity Switch | EK-66-ZSC-6507 | EK_ZSC_6507_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-9 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1102 | 11 | 12 | MC-1 | FRONT | EK-66-JBA-1102 | +11 | -12 | - | OIL-400-EK-I-DW-3033 (Template-T1)
30 | SC-1 | 1 | 0 | 1 | 29 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[29].Value | Proximity Switch | EK-66-ZSO-6508 | EK_ZSO_6508_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-10 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1102 | 13 | 14 | MC-1 | FRONT | EK-66-JBA-1102 | +13 | -14 | - | OIL-400-EK-I-DW-3033 (Template-T1)
31 | SC-1 | 1 | 0 | 1 | 30 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[30].Value | Proximity Switch | EK-66-ZSC-6508 | EK_ZSC_6508_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-10 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1102 | 15 | 16 | MC-1 | FRONT | EK-66-JBA-1102 | +15 | -16 | - | OIL-400-EK-I-DW-3033 (Template-T1)
32 | SC-1 | 1 | 0 | 1 | 31 | BMXDDI3202K | EIO2_d1_r0_s1_DI1.DIS_CH_IN[31].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-14 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1102 | 17 | 18 | MC-1 | FRONT | EK-66-JBA-1102 | +17 | -18 | - | Spare
33 | SC-1 | 1 | 0 | 2 | 0 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[0].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-14 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1102 | 19 | 20 | MC-1 | FRONT | EK-66-JBA-1102 | +19 | -20 | - | Spare
34 | SC-1 | 1 | 0 | 2 | 1 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[1].Value | Proximity Switch | EK-66-ZSO-6509 | EK_ZSO_6509_66 | Air Scouring Inlet in Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-11 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1101 | 17 | 18 | MC-1 | FRONT | EK-66-JBA-1101 | +17 | -18 | - | OIL-400-EK-I-DW-3033 (Template-T1)
35 | SC-1 | 1 | 0 | 2 | 2 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[2].Value | Proximity Switch | EK-66-ZSC-6509 | EK_ZSC_6509_66 | Air Scouring Inlet in Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-11 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1101 | 19 | 20 | MC-1 | FRONT | EK-66-JBA-1101 | +19 | -20 | - | OIL-400-EK-I-DW-3033 (Template-T1)
36 | SC-1 | 1 | 0 | 2 | 3 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[3].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-15 | +1 | -3 | MC-1 | FRONT | EK-66-JBA-1101 | 21 | 22 | MC-1 | FRONT | EK-66-JBA-1101 | +21 | -22 | - | Spare
37 | SC-1 | 1 | 0 | 2 | 4 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[4].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-15 | +4 | -6 | MC-1 | FRONT | EK-66-JBA-1101 | 23 | 24 | MC-1 | FRONT | EK-66-JBA-1101 | +23 | -24 | - | Spare
38 | SC-1 | 1 | 0 | 2 | 5 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[5].Value | Level Switch-Vibration Fork Type | EK-53-LS-4701 | EK_LS_4701_53 | NaoCL Dosing Tank | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-53-JBA-1101 | 1 | 2 | MC-1 | FRONT | EK-53-JBA-1101 | +1 | -2 | - | OIL-400-EK-I-DW-3033 (Template-T2)
39 | SC-1 | 1 | 0 | 2 | 6 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[6].Value | Level Switch-Vibration Fork Type | EK-53-LS-4702 | EK_LS_4702_53 | Acid Dosing Tank | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-53-JBA-1101 | 3 | 4 | MC-1 | FRONT | EK-53-JBA-1101 | +3 | -4 | - | OIL-400-EK-I-DW-3033 (Template-T2)
40 | SC-1 | 1 | 0 | 2 | 7 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[7].Value | Level Switch-Vibration Fork Type | EK-53-LS-4703 | EK_LS_4703_53 | SMBS Dosing Tank | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-53-JBA-1101 | 5 | 6 | MC-1 | FRONT | EK-53-JBA-1101 | +5 | -6 | - | OIL-400-EK-I-DW-3033 (Template-T2)
41 | SC-1 | 1 | 0 | 2 | 8 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[8].Value | Level Switch-Vibration Fork Type | EK-53-LS-4704 | EK_LS_4704_53 | Antiscalant Dosing Tank | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-53-JBA-1101 | 7 | 8 | MC-1 | FRONT | EK-53-JBA-1101 | +7 | -8 | - | OIL-400-EK-I-DW-3033 (Template-T2)
42 | SC-1 | 1 | 0 | 2 | 9 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[9].Value | Motor Run Indication | EK-66-XI-6503 | EK_XI_6503_66 | API Separator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
43 | SC-1 | 1 | 0 | 2 | 10 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[10].Value | Motor Fault Indication | EK-66-XA-6503 | EK_XA_6503_66 | API Separator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
44 | SC-1 | 1 | 0 | 2 | 11 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[11].Value | Motor Trip Indication | EK-66-XB-6503 | EK_XB_6503_66 | API Separator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
45 | SC-1 | 1 | 0 | 2 | 12 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[12].Value | Motor Run Indication | EK-66-XI-6504 | EK_XI_6504_66 | Flash Mixing Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
46 | SC-1 | 1 | 0 | 2 | 13 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[13].Value | Motor Fault Indication | EK-66-XA-6504 | EK_XA_6504_66 | Flash Mixing Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
47 | SC-1 | 1 | 0 | 2 | 14 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[14].Value | Motor Trip Indication | EK-66-XB-6504 | EK_XB_6504_66 | Flash Mixing Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3) | OIL-400-EK-I-DW-3044 (Sheet-07)
48 | SC-1 | 1 | 0 | 2 | 15 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[15].Value | Motor Run Indication | EK-66-XI-6505 | EK_XI_6505_66 | Flocculation Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
49 | SC-1 | 1 | 0 | 2 | 16 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[16].Value | Motor Fault Indication | EK-66-XA-6505 | EK_XA_6505_66 | Flocculation Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 15 | 16 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
50 | SC-1 | 1 | 0 | 2 | 17 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[17].Value | Motor Trip Indication | EK-66-XB-6505 | EK_XB_6505_66 | Flocculation Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 17 | 18 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
51 | SC-1 | 1 | 0 | 2 | 18 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[18].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 19 | 20 | SC-1 | REAR | - | - | - | - | Spare
52 | SC-1 | 1 | 0 | 2 | 19 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[19].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
53 | SC-1 | 1 | 0 | 2 | 20 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[20].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-01 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
54 | SC-1 | 1 | 0 | 2 | 21 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[21].Value | Motor Run Indication | EK-66-XI-6506 | EK_XI_6506_66 | Microbubble Generator Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 1 | 2 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
55 | SC-1 | 1 | 0 | 2 | 22 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[22].Value | Motor Fault Indication | EK-66-XA-6506 | EK_XA_6506_66 | Microbubble Generator Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 3 | 4 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
56 | SC-1 | 1 | 0 | 2 | 23 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[23].Value | Motor Trip Indication | EK-66-XB-6506 | EK_XB_6506_66 | Microbubble Generator Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
57 | SC-1 | 1 | 0 | 2 | 24 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[24].Value | Motor Available Indication | EK-66-XE-6506 | EK_XE_6506_66 | Microbubble Generator Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
58 | SC-1 | 1 | 0 | 2 | 25 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[25].Value | Motor Run Indication | EK-66-XI-6507 | EK_XI_6507_66 | Microbubble Generator Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
59 | SC-1 | 1 | 0 | 2 | 26 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[26].Value | Motor Fault Indication | EK-66-XA-6507 | EK_XA_6507_66 | Microbubble Generator Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
60 | SC-1 | 1 | 0 | 2 | 27 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[27].Value | Motor Trip Indication | EK-66-XB-6507 | EK_XB_6507_66 | Microbubble Generator Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
61 | SC-1 | 1 | 0 | 2 | 28 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[28].Value | Motor Available Indication | EK-66-XE-6507 | EK_XE_6507_66 | Microbubble Generator Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 15 | 16 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
62 | SC-1 | 1 | 0 | 2 | 29 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[29].Value | Motor Run Indication | EK-66-XI-6508 | EK_XI_6508_66 | Filter Feed Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 17 | 18 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
63 | SC-1 | 1 | 0 | 2 | 30 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[30].Value | Motor Fault Indication | EK-66-XA-6508 | EK_XA_6508_66 | Microbubble Generator Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
64 | SC-1 | 1 | 0 | 2 | 31 | BMXDDI3202K | EIO2_d1_r0_s2_DI2.DIS_CH_IN[31].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
65 | SC-1 | 3 | 0 | 1 | 0 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[0].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-02 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
66 | SC-1 | 3 | 0 | 1 | 1 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[1].Value | Motor Run Indication | EK-66-XI-6509 | EK_XI_6509_66 | Filter Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 1 | 2 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
67 | SC-1 | 3 | 0 | 1 | 2 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[2].Value | Motor Fault Indication | EK-66-XA-6509 | EK_XA_6509_66 | Filter Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 3 | 4 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
68 | SC-1 | 3 | 0 | 1 | 3 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[3].Value | Motor Trip Indication | EK-66-XB-6509 | EK_XB_6509_66 | Filter Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
69 | SC-1 | 3 | 0 | 1 | 4 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[4].Value | Motor Available Indication | EK-66-XE-6509 | EK_XE_6509_66 | Filter Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
70 | SC-1 | 3 | 0 | 1 | 5 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[5].Value | Motor Run Indication | EK-66-XI-6510 | EK_XI_6510_66 | Coagulant Dosing Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
71 | SC-1 | 3 | 0 | 1 | 6 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[6].Value | Motor Fault Indication | EK-66-XA-6510 | EK_XA_6510_66 | Coagulant Dosing Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
72 | SC-1 | 3 | 0 | 1 | 7 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[7].Value | Motor Trip Indication | EK-66-XB-6510 | EK_XB_6510_66 | Coagulant Dosing Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
73 | SC-1 | 3 | 0 | 1 | 8 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[8].Value | Motor Available Indication | EK-66-XE-6510 | EK_XE_6510_66 | Coagulant Dosing Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 15 | 16 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
74 | SC-1 | 3 | 0 | 1 | 9 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[9].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 17 | 18 | SC-1 | REAR | - | - | - | - | Spare
75 | SC-1 | 3 | 0 | 1 | 10 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[10].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 19 | 20 | SC-1 | REAR | - | - | - | - | Spare
76 | SC-1 | 3 | 0 | 1 | 11 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[11].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
77 | SC-1 | 3 | 0 | 1 | 12 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[12].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-03 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
78 | SC-1 | 3 | 0 | 1 | 13 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[13].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-53-JBA-1101 | 21 | 22 | MC-1 | FRONT | EK-53-JBA-1101 | 21 | 22 | - | Spare
79 | SC-1 | 3 | 0 | 1 | 14 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[14].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-53-JBA-1101 | 23 | 24 | MC-1 | FRONT | EK-53-JBA-1101 | 23 | 24 | - | Spare
80 | SC-1 | 3 | 0 | 1 | 15 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[15].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 19 | 20 | MC-1 | Front | EK-66-JBA-1104 | - | - | - | Spare
81 | SC-1 | 3 | 0 | 1 | 16 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[16].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 21 | 22 | MC-1 | Front | EK-66-JBA-1104 | - | - | - | Spare
82 | SC-1 | 3 | 0 | 1 | 17 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[17].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-66-JBA-1104 | 23 | 24 | MC-1 | Front | EK-66-JBA-1104 | - | - | - | Spare
83 | SC-1 | 3 | 0 | 1 | 18 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[18].Value | Motor Run Indication | EK-66-XI-6512 | EK_XI_6512_66 | Coagulant Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
84 | SC-1 | 3 | 0 | 1 | 19 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[19].Value | Motor Fault Indication | EK-66-XA-6512 | EK_XA_6512_66 | Coagulant Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
85 | SC-1 | 3 | 0 | 1 | 20 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[20].Value | Motor Trip Indication | EK-66-XB-6512 | EK_XB_6512_66 | Coagulant Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
86 | SC-1 | 3 | 0 | 1 | 21 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[21].Value | Motor Run Indication | EK-66-XI-6513 | EK_XI_6513_66 | PolyElectrolyte Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
87 | SC-1 | 3 | 0 | 1 | 22 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[22].Value | Motor Fault Indication | EK-66-XA-6513 | EK_XA_6513_66 | Poly-Electrolyte Dosing Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
88 | SC-1 | 3 | 0 | 1 | 23 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[23].Value | Motor Trip Indication | EK-66-XB-6513 | EK_XB_6513_66 | Poly-Electrolyte Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
89 | SC-1 | 3 | 0 | 1 | 24 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[24].Value | Motor Available Indication | EK-66-XE-6513 | EK_XE_6513_66 | PolyElectrolyte Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
90 | SC-1 | 3 | 0 | 1 | 25 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[25].Value | Motor Run Indication | EK-66-XI-6514 | EK_XI_6514_66 | Poly-Electrolyte Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
91 | SC-1 | 3 | 0 | 1 | 26 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[26].Value | Motor Fault Indication | EK-66-XA-6514 | EK_XA_6514_66 | Poly-Electrolyte Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 17 | 18 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
92 | SC-1 | 3 | 0 | 1 | 27 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[27].Value | Motor Trip Indication | EK-66-XB-6514 | EK_XB_6514_66 | Poly-Electrolyte Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
93 | SC-1 | 3 | 0 | 1 | 28 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[28].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
94 | SC-1 | 3 | 0 | 1 | 29 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[29].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-04 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
95 | SC-1 | 3 | 0 | 1 | 30 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[30].Value | Motor Run Indication | EK-66-XI-6515 | EK_XI_6515_66 | Poly-Electrolyte Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
96 | SC-1 | 3 | 0 | 1 | 31 | BMXDDI3202K | EIO2_d3_r0_s1_DI3.DIS_CH_IN[31].Value | Motor Fault Indication | EK-66-XA-6515 | EK_XA_6515_66 | Poly-Electrolyte Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
97 | SC-1 | 3 | 0 | 2 | 0 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[0].Value | Motor Trip Indication | EK-66-XB-6515 | EK_XB_6515_66 | Poly-Electrolyte Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
98 | SC-1 | 3 | 0 | 2 | 1 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[1].Value | Motor Run Indication | EK-66-XI-6549 | EK_XI_6549_66 | DAF Unit | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
99 | SC-1 | 3 | 0 | 2 | 2 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[2].Value | Motor Fault Indication | EK-66-XA-6549 | EK_XA_6549_66 | DAF Unit | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
100 | SC-1 | 3 | 0 | 2 | 3 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[3].Value | Motor Trip Indication | EK-66-XB-6549 | EK_XB_6549_66 | DAF Unit | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
101 | SC-1 | 3 | 0 | 2 | 4 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[4].Value | Motor Run Indication | EK-66-XI-6516 | EK_XI_6516_66 | Air Scouring Blower-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
102 | SC-1 | 3 | 0 | 2 | 5 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[5].Value | Motor Fault Indication | EK-66-XA-6516 | EK_XA_6516_66 | Air Scouring Blower-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
103 | SC-1 | 3 | 0 | 2 | 6 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[6].Value | Motor Trip Indication | EK-66-XB-6516 | EK_XB_6516_66 | Air Scouring Blower-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 17 | 18 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
104 | SC-1 | 3 | 0 | 2 | 7 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[7].Value | Motor Available Indication | EK-66-XE-6516 | EK_XE_6516_66 | Air Scouring Blower-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
105 | SC-1 | 3 | 0 | 2 | 8 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[8].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
106 | SC-1 | 3 | 0 | 2 | 9 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[9].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-05 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
107 | SC-1 | 3 | 0 | 2 | 10 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[10].Value | Motor Run Indication | EK-66-XI-6517 | EK_XI_6517_66 | Air Scouring Blower-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-06 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
108 | SC-1 | 3 | 0 | 2 | 11 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[11].Value | Motor Fault Indication | EK-66-XA-6517 | EK_XA_6517_66 | Air Scouring Blower-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-06 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
109 | SC-1 | 3 | 0 | 2 | 12 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[12].Value | Motor Trip Indication | EK-66-XB-6517 | EK_XB_6517_66 | Air Scouring Blower-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-06 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
110 | SC-1 | 3 | 0 | 2 | 13 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[13].Value | Motor Available Indication | EK-66-XE-6517 | EK_XE_6517_66 | Air Scouring Blower-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - |  | EK-66-MCC-DI-06 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
111 | SC-1 | 3 | 0 | 2 | 14 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[14].Value | Motor Run Indication | EK-66-XI-6518 | EK_XI_6518_66 | Clarified Water Disposal Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-06 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
112 | SC-1 | 3 | 0 | 2 | 15 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[15].Value | Motor Fault Indication | EK-66-XA-6518 | EK_XA_6518_66 | Clarified Water Disposal Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-06 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
113 | SC-1 | 3 | 0 | 2 | 16 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[16].Value | Motor Trip Indication | EK-66-XB-6518 | EK_XB_6518_66 | Clarified Water Disposal Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-06 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
114 | SC-1 | 3 | 0 | 2 | 17 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[17].Value | Motor Available Indication | EK-66-XE-6518 | EK_XE_6518_66 | Clarified Water Disposal Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-06 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
115 | SC-1 | 3 | 0 | 2 | 18 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[18].Value | Motor Run Indication | EK-66-XI-6519 | EK_XI_6519_66 | Clarified Water Disposal Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-06 | 17 | 18 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
116 | SC-1 | 3 | 0 | 2 | 19 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[19].Value | Motor Fault Indication | EK-66-XA-6519 | EK_XA_6519_66 | Clarified Water Disposal Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-06 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
117 | SC-1 | 3 | 0 | 2 | 20 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[20].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-06 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
118 | SC-1 | 3 | 0 | 2 | 21 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[21].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-06 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
119 | SC-1 | 3 | 0 | 2 | 22 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[22].Value | Motor Run Indication | EK-66-XI-6520 | EK_XI_6520_66 | Clarified Water Disposal Pump-C | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
120 | SC-1 | 3 | 0 | 2 | 23 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[23].Value | Motor Fault Indication | EK-66-XA-6520 | EK_XA_6520_66 | Clarified Water Disposal Pump-C | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
121 | SC-1 | 3 | 0 | 2 | 24 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[24].Value | Motor Trip Indication | EK-66-XB-6520 | EK_XB_6520_66 | Clarified Water Disposal Pump-C | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
122 | SC-1 | 3 | 0 | 2 | 25 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[25].Value | Motor Available Indication | EK-66-XE-6520 | EK_XE_6520_66 | Clarified Water Disposal Pump-C | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
123 | SC-1 | 3 | 0 | 2 | 26 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[26].Value | Motor Run Indication | EK-66-XI-6521 | EK_XI_6521_66 | Effluent Water Drain Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
124 | SC-1 | 3 | 0 | 2 | 27 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[27].Value | Motor Fault Indication | EK-66-XA-6521 | EK_XA_6521_66 | Effluent Water Drain Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
125 | SC-1 | 3 | 0 | 2 | 28 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[28].Value | Motor Trip Indication | EK-66-XB-6521 | EK_XB_6521_66 | Effluent Water Drain Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
126 | SC-1 | 3 | 0 | 2 | 29 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[29].Value | Motor Available Indication | EK-66-XE-6521 | EK_XE_6521_66 | Effluent Water Drain Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
127 | SC-1 | 3 | 0 | 2 | 30 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[30].Value | Motor Run Indication | EK-66-XI-6522 | EK_XI_6522_66 | Effluent Water Drain Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 17 | 18 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
128 | SC-1 | 3 | 0 | 2 | 31 | BMXDDI3202K | EIO2_d3_r0_s2_DI4.DIS_CH_IN[31].Value | Motor Fault Indication | EK-66-XA-6522 | EK_XA_6522_66 | Effluent Water Drain Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
129 | SC-1 | 3 | 0 | 6 | 0 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[0].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
130 | SC-1 | 3 | 0 | 6 | 1 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[1].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-07 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
131 | SC-1 | 3 | 0 | 6 | 2 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[2].Value | Motor Run Indication | EK-66-XI-6523 | EK_XI_6523_66 | Slop Oil Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
132 | SC-1 | 3 | 0 | 6 | 3 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[3].Value | Motor Fault Indication | EK-66-XA-6523 | EK_XA_6523_66 | Slop Oil Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
133 | SC-1 | 3 | 0 | 6 | 4 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[4].Value | Motor Trip Indication | EK-66-XB-6523 | EK_XB_6523_66 | Slop Oil Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
134 | SC-1 | 3 | 0 | 6 | 5 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[5].Value | Motor Available Indication | EK-66-XE-6523 | EK_XE_6523_66 | Slop Oil Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
135 | SC-1 | 3 | 0 | 6 | 6 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[6].Value | Motor Run Indication | EK-66-XI-6524 | EK_XI_6524_66 | Slop Oil Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
136 | SC-1 | 3 | 0 | 6 | 7 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[7].Value | Motor Fault Indication | EK-66-XA-6524 | EK_XA_6524_66 | Slop Oil Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
137 | SC-1 | 3 | 0 | 6 | 8 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[8].Value | Motor Trip Indication | EK-66-XB-6524 | EK_XB_6524_66 | Slop Oil Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
138 | SC-1 | 3 | 0 | 6 | 9 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[9].Value | Motor Available Indication | EK-66-XE-6524 | EK_XE_6524_66 | Slop Oil Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
139 | SC-1 | 3 | 0 | 6 | 10 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[10].Value | Motor Run Indication | EK-66-XI-6525 | EK_XI_6525_66 | Centrifuge Feed Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 17 | 18 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
140 | SC-1 | 3 | 0 | 6 | 11 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[11].Value | Motor Fault Indication | EK-66-XA-6525 | EK_XA_6525_66 | Centrifuge Feed Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
141 | SC-1 | 3 | 0 | 6 | 12 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[12].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
142 | SC-1 | 3 | 0 | 6 | 13 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[13].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-08 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
143 | SC-1 | 3 | 0 | 6 | 14 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[14].Value | Motor Run Indication | EK-66-XI-6526 | EK_XI_6526_66 | Centrifuge Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
144 | SC-1 | 3 | 0 | 6 | 15 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[15].Value | Motor Fault Indication | EK-66-XA-6526 | EK_XA_6526_66 | Centrifuge Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
145 | SC-1 | 3 | 0 | 6 | 16 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[16].Value | Motor Trip Indication | EK-66-XB-6526 | EK_XB_6526_66 | Centrifuge Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
146 | SC-1 | 3 | 0 | 6 | 17 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[17].Value | Motor Available Indication | EK-66-XE-6526 | EK_XE_6526_66 | Centrifuge Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
147 | SC-1 | 3 | 0 | 6 | 18 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[18].Value | Motor Run Indication | EK-66-XI-6527 | EK_XI_6527_66 | Centrifuge | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
148 | SC-1 | 3 | 0 | 6 | 19 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[19].Value | Motor Fault Indication | EK-66-XA-6527 | EK_XA_6527_66 | Centrifuge | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
149 | SC-1 | 3 | 0 | 6 | 20 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[20].Value | Motor Trip Indication | EK-66-XB-6527 | EK_XB_6527_66 | Centrifuge | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
150 | SC-1 | 3 | 0 | 6 | 21 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[21].Value | Motor Run Indication | EK-66-XI-6528 | EK_XI_6528_66 | DWPE Dosign Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
151 | SC-1 | 3 | 0 | 6 | 22 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[22].Value | Motor Fault Indication | EK-66-XA-6528 | EK_XA_6528_66 | DWPE Dosign Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 17 | 18 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
152 | SC-1 | 3 | 0 | 6 | 23 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[23].Value | Motor Trip Indication | EK-66-XB-6528 | EK_XB_6528_66 | DWPE Dosign Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
153 | SC-1 | 3 | 0 | 6 | 24 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[24].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
154 | SC-1 | 3 | 0 | 6 | 25 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[25].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-09 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
155 | SC-1 | 3 | 0 | 6 | 26 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[26].Value | Motor Run Indication | EK-66-XI-6529 | EK_XI_6529_66 | DWPE Dosign Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
156 | SC-1 | 3 | 0 | 6 | 27 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[27].Value | Motor Fault Indication | EK-66-XA-6529 | EK_XA_6529_66 | DWPE Dosign Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
157 | SC-1 | 3 | 0 | 6 | 28 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[28].Value | Motor Trip Indication | EK-66-XB-6529 | EK_XB_6529_66 | DWPE Dosign Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
158 | SC-1 | 3 | 0 | 6 | 29 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[29].Value | Motor Run Indication | EK-66-XI-6530 | EK_XI_6530_66 | DWPE Dosign Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
159 | SC-1 | 3 | 0 | 6 | 30 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[30].Value | Motor Fault Indication | EK-66-XA-6530 | EK_XA_6530_66 | DWPE Dosign Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
160 | SC-1 | 3 | 0 | 6 | 31 | BMXDDI3202K | EIO2_d3_r0_s7_DI5.DIs_CH_IN[31].Value | Motor Trip Indication | EK-66-XB-6530 | EK_XB_6530_66 | DWPE Dosign Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
161 | SC-1 | 3 | 0 | 7 | 0 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[0].Value | Motor Available Indication | EK-66-XE-6530 | EK_XE_6530_66 | DWPE Dosign Tank Agitator | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
162 | SC-1 | 3 | 0 | 7 | 1 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[1].Value | Motor Run Indication | EK-66-XI-6531 | EK_XI_6531_66 | Skim Oil transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
163 | SC-1 | 3 | 0 | 7 | 2 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[2].Value | Motor Fault Indication | EK-66-XA-6531 | EK_XA_6531_66 | Skim Oil transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 17 | 18 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
164 | SC-1 | 3 | 0 | 7 | 3 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[3].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 19 | 20 | SC-1 | REAR | - | - | - | - | Spare
165 | SC-1 | 3 | 0 | 7 | 4 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[4].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
166 | SC-1 | 3 | 0 | 7 | 5 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[5].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-10 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
167 | SC-1 | 3 | 0 | 7 | 6 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[6].Value | Motor Run Indication | EK-66-XI-6532 | EK_XI_6532_66 | Skim Oil transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
168 | SC-1 | 3 | 0 | 7 | 7 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[7].Value | Motor Fault Indication | EK-66-XA-6532 | EK_XA_6532_66 | Skim Oil transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
169 | SC-1 | 3 | 0 | 7 | 8 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[8].Value | Motor Trip Indication | EK-66-XB-6532 | EK_XB_6532_66 | Skim Oil transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
170 | SC-1 | 3 | 0 | 7 | 9 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[9].Value | Motor Available Indication | EK-66-XE-6532 | EK_XE_6532_66 | Skim Oil transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
171 | SC-1 | 3 | 0 | 7 | 10 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[10].Value | Motor Run Indication | EK-66-XI-6533 | EK_XI_6533_66 | Off-Spec Effluent Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
172 | SC-1 | 3 | 0 | 7 | 11 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[11].Value | Motor Fault Indication | EK-66-XA-6533 | EK_XA_6533_66 | Off-Spec Effluent Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
173 | SC-1 | 3 | 0 | 7 | 12 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[12].Value | Motor Trip Indication | EK-66-XB-6533 | EK_XB_6533_66 | Off-Spec Effluent Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
174 | SC-1 | 3 | 0 | 7 | 13 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[13].Value | Motor Available Indication | EK-66-XE-6533 | EK_XE_6533_66 | Off-Spec Effluent Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
175 | SC-1 | 3 | 0 | 7 | 14 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[14].Value | Motor Fault Indication | EK-66-XA-6534 | EK_XA_6534_66 | Off-Spec Effluent Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 17 | 18 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
176 | SC-1 | 3 | 0 | 7 | 15 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[15].Value | Motor Run Indication | EK-66-XI-6534 | EK_XI_6534_66 | Off-Spec Effluent Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
177 | SC-1 | 3 | 0 | 7 | 16 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[16].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
178 | SC-1 | 3 | 0 | 7 | 17 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[17].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-11 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
179 | SC-1 | 3 | 0 | 7 | 18 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[18].Value | Motor Run Indication | EK-66-XI-6537 | EK_XI_6537_66 | Sewage Lift Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
180 | SC-1 | 3 | 0 | 7 | 19 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[19].Value | Motor Fault Indication | EK-66-XA-6537 | EK_XA_6537_66 | Sewage Lift Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
181 | SC-1 | 3 | 0 | 7 | 20 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[20].Value | Motor Trip Indication | EK-66-XB-6537 | EK_XB_6537_66 | Sewage Lift Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
182 | SC-1 | 3 | 0 | 7 | 21 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[21].Value | Motor Available Indication | EK-66-XE-6537 | EK_XE_6537_66 | Sewage Lift Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
183 | SC-1 | 3 | 0 | 7 | 22 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[22].Value | Motor Run Indication | EK-66-XI-6538 | EK_XI_6538_66 | Sewage Lift Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
184 | SC-1 | 3 | 0 | 7 | 23 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[23].Value | Motor Fault Indication | EK-66-XA-6538 | EK_XA_6538_66 | Sewage Lift Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
185 | SC-1 | 3 | 0 | 7 | 24 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[24].Value | Motor Trip Indication | EK-66-XB-6538 | EK_XB_6538_66 | Sewage Lift Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
186 | SC-1 | 3 | 0 | 7 | 25 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[25].Value | Motor Available Indication | EK-66-XE-6538 | EK_XE_6538_66 | Sewage Lift Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
187 | SC-1 | 3 | 0 | 7 | 26 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[26].Value | Motor Run Indication | EK-66-XI-6539 | EK_XI_6539_66 | Sludge Recyclic Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 17 | 18 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
188 | SC-1 | 3 | 0 | 7 | 27 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[27].Value | Motor Fault Indication | EK-66-XA-6539 | EK_XA_6539_66 | Sludge Recyclic Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
189 | SC-1 | 3 | 0 | 7 | 28 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[28].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
190 | SC-1 | 3 | 0 | 7 | 29 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[29].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-12 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
191 | SC-1 | 3 | 0 | 7 | 30 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[30].Value | Motor Run Indication | EK-66-XI-6540 | EK_XI_6540_66 | Sludge Recyclic Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
192 | SC-1 | 3 | 0 | 7 | 31 | BMXDDI3202K | EIO2_d3_r0_s8_DI6.DIs_CH_IN[31].Value | Motor Fault Indication | EK-66-XA-6540 | EK_XA_6540_66 | Sludge Recyclic Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
193 | SC-1 | 3 | 0 | 8 | 0 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[0].Value | Motor Trip Indication | EK-66-XB-6540 | EK_XB_6540_66 | Sludge Recyclic Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
194 | SC-1 | 3 | 0 | 8 | 1 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[1].Value | Motor Available Indication | EK-66-XE-6540 | EK_XE_6540_66 | Sludge Recyclic Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
195 | SC-1 | 3 | 0 | 8 | 2 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[2].Value | Motor Run Indication | EK-66-XI-6541 | EK_XI_6541_66 | Air Blower-A for Aeration Tank | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
196 | SC-1 | 3 | 0 | 8 | 3 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[3].Value | Motor Fault Indication | EK-66-XA-6541 | EK_XA_6541_66 | Air Blower-A for Aeration Tank | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
197 | SC-1 | 3 | 0 | 8 | 4 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[4].Value | Motor Trip Indication | EK-66-XB-6541 | EK_XB_6541_66 | Air Blower-A for Aeration Tank | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
198 | SC-1 | 3 | 0 | 8 | 5 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[5].Value | Motor Available Indication | EK-66-XE-6541 | EK_XE_6541_66 | Air Blower-A for Aeration Tank | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
199 | SC-1 | 3 | 0 | 8 | 6 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[6].Value | Motor Run Indication | EK-66-XI-6542 | EK_XI_6542_66 | Air Blower-B for Aeration Tank | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 17 | 18 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
200 | SC-1 | 3 | 0 | 8 | 7 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[7].Value | Motor Fault Indication | EK-66-XA-6542 | EK_XA_6542_66 | Air Blower-B for Aeration Tank | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
201 | SC-1 | 3 | 0 | 8 | 8 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[8].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
202 | SC-1 | 3 | 0 | 8 | 9 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[9].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-13 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
203 | SC-1 | 3 | 0 | 8 | 10 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[10].Value | Motor Run Indication | EK-66-XI-6543 | EK_XI_6543_66 | Filter Feed Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
204 | SC-1 | 3 | 0 | 8 | 11 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[11].Value | Motor Fault Indication | EK-66-XA-6543 | EK_XA_6543_66 | Filter Feed Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
205 | SC-1 | 3 | 0 | 8 | 12 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[12].Value | Motor Trip Indication | EK-66-XB-6543 | EK_XB_6543_66 | Filter Feed Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
206 | SC-1 | 3 | 0 | 8 | 13 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[13].Value | Motor Available Indication | EK-66-XE-6543 | EK_XE_6543_66 | Filter Feed Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
207 | SC-1 | 3 | 0 | 8 | 14 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[14].Value | Motor Run Indication | EK-66-XI-6544 | EK_XI_6544_66 | Filter Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
208 | SC-1 | 3 | 0 | 8 | 15 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[15].Value | Motor Fault Indication | EK-66-XA-6544 | EK_XA_6544_66 | Filter Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
209 | SC-1 | 3 | 0 | 8 | 16 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[16].Value | Motor Trip Indication | EK-66-XB-6544 | EK_XB_6544_66 | Filter Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
210 | SC-1 | 3 | 0 | 8 | 17 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[17].Value | Motor Available Indication | EK-66-XE-6544 | EK_XE_6544_66 | Filter Feed Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
211 | SC-1 | 3 | 0 | 8 | 18 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[18].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 17 | 18 | SC-1 | REAR |  |  |  | - | Spare
212 | SC-1 | 3 | 0 | 8 | 19 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[19].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 19 | 20 | SC-1 | REAR | - | - | - | - | Spare
213 | SC-1 | 3 | 0 | 8 | 20 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[20].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
214 | SC-1 | 3 | 0 | 8 | 21 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[21].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-14 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
215 | SC-1 | 3 | 0 | 8 | 22 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[22].Value | Motor Run Indication | EK-66-XA-6545 | EK_XI_6545_66 | Naocl Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-15 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
216 | SC-1 | 3 | 0 | 8 | 23 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[23].Value | Motor Fault Indication | EK-66-XA-6545 | EK_XA_6545_66 | Naocl Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-15 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
217 | SC-1 | 3 | 0 | 8 | 24 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[24].Value | Motor Trip Indication | EK-66-XA-6545 | EK_XB_6545_66 | Naocl Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-15 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
218 | SC-1 | 3 | 0 | 8 | 25 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[25].Value | Motor Run Indication | EK-66-XA-6546 | EK_XI_6546_66 | Naocl Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-15 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
219 | SC-1 | 3 | 0 | 8 | 26 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[26].Value | Motor Fault Indication | EK-66-XA-6546 | EK_XA_6546_66 | Naocl Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-15 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
220 | SC-1 | 3 | 0 | 8 | 27 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[27].Value | Motor Trip Indication | EK-66-XA-6546 | EK_XB_6546_66 | Naocl Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-15 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
221 | SC-1 | 3 | 0 | 8 | 28 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[28].Value | Level Trasmitter Relay Contact | EK-MPC3-DI5 | EK_MPC3_DI5 | Clarified Water storage tank Low Low Level | Discrete | - | DI | Potential Free Contact | - | - | - | - | Client | Control Room | EK-66-MCC-DI-15 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
222 | SC-1 | 3 | 0 | 8 | 29 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[29].Value | Level Trasmitter Relay Contact | EK-MPC3-DI6 | EK_MPC3_DI6 | kim Oil Tank Low Low Level | Discrete | - | DI | Potential Free Contact | - | - | - | - | Client | Control Room | EK-66-MCC-DI-15 | 15 | 16 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
223 | SC-1 | 3 | 0 | 8 | 30 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[30].Value | Level Trasmitter Relay Contact | EK-MPC3-DI7 | EK_MPC3_DI7 | Off Spec Effluent Water Storage Tank Low Low Level | Discrete | - | DI | Potential Free Contact | - | - | - | - | Client | Control Room | EK-66-MCC-DI-15 | 17 | 18 | SC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
224 | SC-1 | 3 | 0 | 8 | 31 | BMXDDI3202K | EIO2_d3_r0_s9_DI7.DIs_CH_IN[31].Value | Level Trasmitter Relay Contact | EK-MPC3-DI8 | EK_MPC3_DI8 | Master ESD system Trip | Discrete | - | DI | Potential Free Contact | - | - | - | - | Client | Control Room | EK-66-MCC-DI-15 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
225 | SC-1 | 3 | 0 | 9 | 0 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[0].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-15 | 21 | 22 | SC-1 | REAR | - | - | - | - | Spare
226 | SC-1 | 3 | 0 | 9 | 1 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[1].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-15 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
227 | SC-1 | 3 | 0 | 9 | 2 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[2].Value | Motor Run Indication | EK-66-XI-6547 | EK_XI_6547_66 | Treated Water Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 1 | 2 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
228 | SC-1 | 3 | 0 | 9 | 3 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[3].Value | Motor Fault Indication | EK-66-XA-6547 | EK_XA_6547_66 | Treated Water Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 3 | 4 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
229 | SC-1 | 3 | 0 | 9 | 4 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[4].Value | Motor Trip Indication | EK-66-XB-6547 | EK_XB_6547_66 | Treated Water Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 5 | 6 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
230 | SC-1 | 3 | 0 | 9 | 5 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[5].Value | Motor Available Indication | EK-66-XE--6547 | EK_XE_6547_66 | Treated Water Transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 7 | 8 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
231 | SC-1 | 3 | 0 | 9 | 6 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[6].Value | Motor Run Indication | EK-66-XI-6548 | EK_XI_6548_66 | Treated Water Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 9 | 10 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
232 | SC-1 | 3 | 0 | 9 | 7 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[7].Value | Motor Fault Indication | EK-66-XA-6548 | EK_XA_6548_66 | Treated Water Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 11 | 12 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
233 | SC-1 | 3 | 0 | 9 | 8 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[8].Value | Motor Trip Indication | EK-66-XB-6548 | EK_XB_6548_66 | Treated Water Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 13 | 14 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
234 | SC-1 | 3 | 0 | 9 | 9 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[9].Value | Motor Available Indication | EK-66-XE-6548 | EK_XE_6548_66 | Treated Water Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 15 | 16 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
235 | SC-1 | 3 | 0 | 9 | 10 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[10].Value | Motor Run Indication | EK-66-XI-6511 | EK_XI_6511_66 | Coagulant Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 17 | 18 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
236 | SC-1 | 3 | 0 | 9 | 11 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[11].Value | Motor Fault Indication | EK-66-XA-6511 | EK_XA_6511_66 | Coagulant Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 19 | 20 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
237 | SC-1 | 3 | 0 | 9 | 12 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[12].Value | Motor Trip Indication | EK-66-XB-6511 | EK_XB_6511_66 | Coagulant Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 21 | 22 | SC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
238 | SC-1 | 3 | 0 | 9 | 13 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[13].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-16 | 23 | 24 | SC-1 | REAR | - | - | - | - | Spare
239 | SC-1 | 3 | 0 | 9 | 14 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[14].Value | Motor Trip Indication | EK-66-XB-6508 | EK_XB_6508_66 | Filter Feed Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-17 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
240 | SC-1 | 3 | 0 | 9 | 15 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[15].Value | Motor Available Indication | EK-66-XE-6508 | EK_XE_6508_66 | Filter Feed Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-17 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
241 | SC-1 | 3 | 0 | 9 | 16 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[16].Value | Motor Trip Indication | EK-66-XB-6519 | EK_XB_6519_66 | Clarified Water Disposal Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-17 | 5 | 6 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
242 | SC-1 | 3 | 0 | 9 | 17 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[17].Value | Motor Available Indication | EK-66-XE-6519 | EK_XE_6519_66 | Clarified Water Disposal Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-17 | 7 | 8 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
243 | SC-1 | 3 | 0 | 9 | 18 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[18].Value | Motor Trip Indication | EK-66-XB-6522 | EK_XB_6522_66 | Effluent Water Drain Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-17 | 9 | 10 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
244 | SC-1 | 3 | 0 | 9 | 19 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[19].Value | Motor Available Indication | EK-66-XE-6522 | EK_XE_6522_66 | Effluent Water Drain Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-17 | 11 | 12 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
245 | SC-1 | 3 | 0 | 9 | 20 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[20].Value | Motor Trip Indication | EK-66-XB-6525 | EK_XB_6525_66 | Centrifuge Feed Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-17 | 13 | 14 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
246 | SC-1 | 3 | 0 | 9 | 21 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[21].Value | Motor Available Indication | EK-66-XE-6525 | EK_XE_6525_66 | Centrifuge Feed Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-17 | 15 | 16 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
247 | SC-1 | 3 | 0 | 9 | 22 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[22].Value | Motor Trip Indication | EK-66-XB-6531 | EK_XB_6531_66 | Skim Oil transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-17 | 17 | 18 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
248 | SC-1 | 3 | 0 | 9 | 23 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[23].Value | Motor Available Indication | EK-66-XE-6531 | EK_XE_6531_66 | Skim Oil transfer Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-17 | 19 | 20 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
249 | SC-1 | 3 | 0 | 9 | 24 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[24].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Potential Free Contact | - | - | - | - | - | - | EK-66-MCC-DI-17 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
250 | SC-1 | 3 | 0 | 9 | 25 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[25].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Potential Free Contact | - | - | - | - | - | - | EK-66-MCC-DI-17 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
251 | SC-1 | 3 | 0 | 9 | 26 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[26].Value | Motor Trip Indication | EK-66-XB-6534 | EK_XB_6534_66 | Off-Spec Effluent Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-18 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
252 | SC-1 | 3 | 0 | 9 | 27 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[27].Value | Motor Available Indication | EK-66-XE-6534 | EK_XE_6534_66 | Off-Spec Effluent Transfer Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-18 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
253 | SC-1 | 3 | 0 | 9 | 28 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[28].Value | Motor Trip Indication | EK-66-XB-6539 | EK_XB_6539_66 | Sludge Recyclic Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-18 | 5 | 6 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
254 | SC-1 | 3 | 0 | 9 | 29 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[29].Value | Motor Available Indication | EK-66-XE-6539 | EK_XE_6539_66 | Sludge Recyclic Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-18 | 7 | 8 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
255 | SC-1 | 3 | 0 | 9 | 30 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[30].Value | Motor Trip Indication | EK-66-XB-6542 | EK_XB_6542_66 | Air Blower-B for Aeration Tank | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-18 | 9 | 10 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
256 | SC-1 | 3 | 0 | 9 | 31 | BMXDDI3202K | EIO2_d3_r0_s10_DI8.DIs_CH_IN[31].Value | Motor Available Indication | EK-66-XE-6542 | EK_XE_6542_66 | Air Blower-B for Aeration Tank | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-66-MCC-DI-18 | 11 | 12 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
257 | SC-1 | 3 | 1 | 0 | 0 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[0].Value | Level Trasmitter Relay Contact | EK-MPC3-DI1 | EK_MPC3_DI1 | Potable water tank High High Level | Discrete | - | DI | Potential Free Contact | - | - | - | - | Client | Control Room | EK-66-MCC-DI-18 | 13 | 14 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
258 | SC-1 | 3 | 1 | 0 | 1 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[1].Value | Level Trasmitter Relay Contact | EK-MPC3-DI2 | EK_MPC3_DI2 | Effluent water storage tank High High Level | Discrete | - | DI | Potential Free Contact | - | - | - | - | Client | Control Room | EK-66-MCC-DI-18 | 15 | 16 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
259 | SC-1 | 3 | 1 | 0 | 2 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[2].Value | Level Trasmitter Relay Contact | EK-MPC3-DI3 | EK_MPC3_DI3 | Skim oil tank high high Level | Discrete | - | DI | Potential Free Contact | - | - | - | - | Client | Control Room | EK-66-MCC-DI-18 | 17 | 18 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
260 | SC-1 | 3 | 1 | 0 | 3 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[3].Value | Level Trasmitter Relay Contact | EK-MPC3-DI4 | EK_MPC3_DI4 | Master ESD system Trip | Discrete | - | DI | Potential Free Contact | - | - | - | - | Client | Control Room | EK-66-MCC-DI-18 | 19 | 20 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
261 | SC-1 | 3 | 1 | 0 | 4 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[4].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Potential Free Contact | - | - | - | - | - | - | EK-66-MCC-DI-18 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
262 | SC-1 | 3 | 1 | 0 | 5 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[5].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Potential Free Contact | - | - | - | - | - | - | EK-66-MCC-DI-18 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
263 | SC-1 | 3 | 1 | 0 | 6 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[6].Value | Motor Run Indication | EK-53-XI-4701 | EK_XI_4701_53 | NaoCl Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - |  | EK-53-MCC-DI-01 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
264 | SC-1 | 3 | 1 | 0 | 7 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[7].Value | Motor Fault Indication | EK-53-XA-4701 | EK_XA_4701_53 | NaoCl Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-01 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
265 | SC-1 | 3 | 1 | 0 | 8 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[8].Value | Motor Trip Indication | EK-53-XB-4701 | EK_XB_4701_53 | NaoCl Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-01 | 5 | 6 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
266 | SC-1 | 3 | 1 | 0 | 9 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[9].Value | Motor Run Indication | EK-53-XI-4702 | EK_XI_4702_53 | NaoCl Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-01 | 7 | 8 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
267 | SC-1 | 3 | 1 | 0 | 10 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[10].Value | Motor Fault Indication | EK-53-XA-4702 | EK_XA_4702_53 | NaoCl Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-01 | 9 | 10 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
268 | SC-1 | 3 | 1 | 0 | 11 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[11].Value | Motor Trip Indication | EK-53-XB-4702 | EK_XB_4702_53 | NaoCl Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-01 | 11 | 12 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
269 | SC-1 | 3 | 1 | 0 | 12 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[12].Value | Motor Run Indication | EK-53-XI-4703 | EK_XI_4703_53 | Acid-Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-01 | 13 | 14 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
270 | SC-1 | 3 | 1 | 0 | 13 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[13].Value | Motor Fault Indication | EK-53-XA-4703 | EK_XA_4703_53 | Acid-Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-01 | 15 | 16 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
271 | SC-1 | 3 | 1 | 0 | 14 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[14].Value | Motor Trip Indication | EK-53-XB-4703 | EK_XB_4703_53 | Acid-Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-01 | 17 | 18 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
272 | SC-1 | 3 | 1 | 0 | 15 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[15].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - |  | EK-53-MCC-DI-01 | 19 | 20 | MC-1 | REAR | - | - | - | - | Spare
273 | SC-1 | 3 | 1 | 0 | 16 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[16].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - |  | EK-53-MCC-DI-01 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
274 | SC-1 | 3 | 1 | 0 | 17 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[17].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - |  | EK-53-MCC-DI-01 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
275 | SC-1 | 3 | 1 | 0 | 18 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[18].Value | Motor Run Indication | EK-53-XI-4704 | EK_XI_4704_53 | Acid-Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
276 | SC-1 | 3 | 1 | 0 | 19 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[19].Value | Motor Fault Indication | EK-53-XA-4704 | EK_XA_4704_53 | Acid-Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
277 | SC-1 | 3 | 1 | 0 | 20 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[20].Value | Motor Trip Indication | EK-53-XB--4704 | EK_XB_4704_53 | Acid-Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 5 | 6 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
278 | SC-1 | 3 | 1 | 0 | 21 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[21].Value | Motor Run Indication | EK-53-XI--4705 | EK_XI_4705_53 | SMBS Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 7 | 8 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
279 | SC-1 | 3 | 1 | 0 | 22 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[22].Value | Motor Fault Indication | EK-53-XA-4705 | EK_XA_4705_53 | SMBS Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 9 | 10 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
280 | SC-1 | 3 | 1 | 0 | 23 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[23].Value | Motor Trip Indication | EK-53-XB-4705 | EK_XB_4705_53 | SMBS Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 11 | 12 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
281 | SC-1 | 3 | 1 | 0 | 24 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[24].Value | Motor Run Indication | EK-53-XI-4706 | EK_XI_4706_53 | SMBS Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 13 | 14 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
282 | SC-1 | 3 | 1 | 0 | 25 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[25].Value | Motor Fault Indication | EK-53-XA-4706 | EK_XA_4706_53 | SMBS Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 15 | 16 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
283 | SC-1 | 3 | 1 | 0 | 26 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[26].Value | Motor Trip Indication | EK-53-XB-4706 | EK_XB_4706_53 | SMBS Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 17 | 18 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
284 | SC-1 | 3 | 1 | 0 | 27 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[27].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 19 | 20 | MC-1 | REAR | - | - | - | - | Spare
285 | SC-1 | 3 | 1 | 0 | 28 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[28].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
286 | SC-1 | 3 | 1 | 0 | 29 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[29].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-02 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
287 | SC-1 | 3 | 1 | 0 | 30 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[30].Value | Motor Run Indication | EK-53-XI-4707 | EK_XI_4707_53 | Anti-Scalant Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
288 | SC-1 | 3 | 1 | 0 | 31 | BMXDDI3202K | EIO2_d3_r1_s0_DI9.DIs_CH_IN[31].Value | Motor Fault Indication | EK-53-XA-4707 | EK_XA_4707_53 | Anti-Scalant Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
289 | SC-1 | 3 | 1 | 1 | 0 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[0].Value | Motor Trip Indication | EK-53-XB-4707 | EK_XB_4707_53 | Anti-Scalant Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 5 | 6 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
290 | SC-1 | 3 | 1 | 1 | 1 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[1].Value | Motor Run Indication | EK-53-XI-4708 | EK_XI_4708_53 | Anti-Scalant Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 7 | 8 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
291 | SC-1 | 3 | 1 | 1 | 2 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[2].Value | Motor Fault Indication | EK-53-XA-4708 | EK_XA_4708_53 | Anti-Scalant Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 9 | 10 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
292 | SC-1 | 3 | 1 | 1 | 3 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[3].Value | Motor Trip Indication | EK-53-XB-4708 | EK_XB_4708_53 | Anti-Scalant Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 11 | 12 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
293 | SC-1 | 3 | 1 | 1 | 4 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[4].Value | Motor Run Indication | EK-53-XI-4709 | EK_XI_4709_53 | Caustic Dosing Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 13 | 14 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
294 | SC-1 | 3 | 1 | 1 | 5 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[5].Value | Motor Fault Indication | EK-53-XA-4709 | EK_XA_4709_53 | Caustic Dosing Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 15 | 16 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
295 | SC-1 | 3 | 1 | 1 | 6 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[6].Value | Motor Trip Indication | EK-53-XB-4709 | EK_XB_4709_53 | Caustic Dosing Dosing Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 17 | 18 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
296 | SC-1 | 3 | 1 | 1 | 7 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[7].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 19 | 20 | MC-1 | REAR | - | - | - | - | Spare
297 | SC-1 | 3 | 1 | 1 | 8 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[8].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
298 | SC-1 | 3 | 1 | 1 | 9 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[9].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-03 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
299 | SC-1 | 3 | 1 | 1 | 10 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[10].Value | Motor Run Indication | EK-53-XI-4710 | EK_XI_4710_53 | Caustic Dosing Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
300 | SC-1 | 3 | 1 | 1 | 11 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[11].Value | Motor Fault Indication | EK-53-XA-4710 | EK_XA_4710_53 | Caustic Dosing Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
301 | SC-1 | 3 | 1 | 1 | 12 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[12].Value | Motor Trip Indication | EK-53-XB-4710 | EK_XB_4710_53 | Caustic Dosing Dosing Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 5 | 6 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
302 | SC-1 | 3 | 1 | 1 | 13 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[13].Value | Motor Run Indication | EK-53-XI-4711 | EK_XI_4711_53 | RO High Pressure Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 7 | 8 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
303 | SC-1 | 3 | 1 | 1 | 14 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[14].Value | Motor Fault Indication | EK-53-XA-4711 | EK_XA_4711_53 | RO High Pressure Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 9 | 10 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
304 | SC-1 | 3 | 1 | 1 | 15 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[15].Value | Motor Trip Indication | EK-53-XB-4711 | EK_XB_4711_53 | RO High Pressure Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 11 | 12 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
305 | SC-1 | 3 | 1 | 1 | 16 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[16].Value | Motor Available Indication | EK-53-XE-4711 | EK_XE_4711_53 | RO High Pressure Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 13 | 14 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
306 | SC-1 | 3 | 1 | 1 | 17 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[17].Value | Motor Run Indication | EK-53-XI-4712 | EK_XI_4712_53 | RO High Pressure Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 15 | 16 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
307 | SC-1 | 3 | 1 | 1 | 18 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[18].Value | Motor Fault Indication | EK-53-XA-4712 | EK_XA_4712_53 | RO High Pressure Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 17 | 18 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
308 | SC-1 | 3 | 1 | 1 | 19 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[19].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 19 | 20 | MC-1 | REAR | - | - | - | - | Spare
309 | SC-1 | 3 | 1 | 1 | 20 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[20].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
310 | SC-1 | 3 | 1 | 1 | 21 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[21].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-04 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
311 | SC-1 | 3 | 1 | 1 | 22 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[22].Value | Motor Run Indication | EK-53-XI-4713 | EK_XI_4713_53 | RO CIP Pump | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
312 | SC-1 | 3 | 1 | 1 | 23 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[23].Value | Motor Fault Indication | EK-53-XA-4713 | EK_XA_4713_53 | RO CIP Pump | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
313 | SC-1 | 3 | 1 | 1 | 24 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[24].Value | Motor Trip Indication | EK-53-XB-4713 | EK_XB_4713_53 | RO CIP Pump | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 5 | 6 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
314 | SC-1 | 3 | 1 | 1 | 25 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[25].Value | Motor Run Indication | EK-53-XI-4714 | EK_XI_4714_53 | Potable Water Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 7 | 8 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
315 | SC-1 | 3 | 1 | 1 | 26 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[26].Value | Motor Fault Indication | EK-53-XA-4714 | EK_XA_4714_53 | Potable Water Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 9 | 10 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
316 | SC-1 | 3 | 1 | 1 | 27 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[27].Value | Motor Trip Indication | EK-53-XB-4714 | EK_XB_4714_53 | Potable Water Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 11 | 12 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
317 | SC-1 | 3 | 1 | 1 | 28 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[28].Value | Motor Available Indication | EK-53-XE-4714 | EK_XE_4714_53 | Potable Water Pump-A | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 13 | 14 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
318 | SC-1 | 3 | 1 | 1 | 29 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[29].Value | Motor Run Indication | EK-53-XI-4715 | EK_XI_4715_53 | Potable Water Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 15 | 16 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
319 | SC-1 | 3 | 1 | 1 | 30 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[30].Value | Motor Fault Indication | EK-53-XA-4715 | EK_XA_4715_53 | Potable Water Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 17 | 18 | MC-1 | REAR |  |  |  | - | OIL-400-EK-I-DW-3033 (Template-T3)
320 | SC-1 | 3 | 1 | 1 | 31 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[31].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 19 | 20 | MC-1 | REAR | - | - | - | - | Spare
321 | SC-1 | 3 | 1 | 2 | 0 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[0].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
322 | SC-1 | 3 | 1 | 2 | 1 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[1].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-05 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
323 | SC-1 | 3 | 1 | 2 | 2 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[2].Value | Motor Trip Indication | EK-53-XB-4712 | EK_XB_4712_53 | RO High Pressure Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-06 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
324 | SC-1 | 3 | 1 | 2 | 3 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[3].Value | Motor Available Indication | EK-53-XE-4712 | EK_XE_4712_53 | RO High Pressure Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-06 | 3 | 4 | MC-1 | Rear | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
325 | SC-1 | 3 | 1 | 2 | 4 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[4].Value | Motor Trip Indication | EK-53-XB-4715 | EK_XB_4715_53 | Potable Water Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-06 | 5 | 6 | MC-1 | Rear | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
326 | SC-1 | 3 | 1 | 2 | 5 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[5].Value | Motor Available Indication | EK-53-XE-4715 | EK_XE_4715_53 | Potable Water Pump-B | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-06 | 7 | 8 | MC-1 | Rear | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T3)
327 | SC-1 | 3 | 1 | 2 | 6 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[6].Value | EK-PS3-FAIL | EK-PS3-FAIL | EK_PS3_FAIL | Bulk Power Supply Failure (3&4) | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T11)
328 | SC-1 | 3 | 1 | 2 | 7 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[7].Value | EK-PS5-FAIL | EK-PS5-FAIL | EK_PS5_FAIL | Bulk Power Supply Failure (5&6) | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T11)
329 | SC-1 | 3 | 1 | 2 | 8 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[8].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-06 | 13 | 14 | MC-1 | Rear | - | - | - | - | Spare
330 | SC-1 | 3 | 1 | 2 | 9 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[9].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | MCC-Contact Type Input (Wet Contact -24VDC) | - | - | - | - | - | - | EK-53-MCC-DI-06 | 15 | 16 | MC-1 | Rear | - | - | - | - | Spare
331 | SC-1 | 3 | 1 | 2 | 10 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[10].Value | Level Switch-Displacer Type | EK-53-LS-4706 | EK_LS_4706_53 | RO CIP Tank | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-53-JBA-1101 | 11 | 12 | MC-1 | FRONT | EK-53-JBA-1101 | +11 | -12 | - | OIL-400-EK-I-DW-3033 (Template-T2)
332 | SC-1 | 3 | 1 | 2 | 11 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[11].Value | Pressure Switch | EK-53-PS-4701 | EK_PS_4701_53 | RO High Pressure Pump Intlet (EK-PBA-4707A/B) | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-53-JBA-1101 | 13 | 14 | MC-1 | FRONT | EK-53-JBA-1101 | +13 | -14 | - | OIL-400-EK-I-DW-3033 (Template-T2)
333 | SC-1 | 3 | 1 | 2 | 12 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[12].Value | Pressure Switch | EK-53-PS-4702 | EK_PS_4702_53 | RO High Pressure Pump Outlet (EK-PBA-4707A/B) | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-53-JBA-1101 | 15 | 16 | MC-1 | FRONT | EK-53-JBA-1101 | +15 | -16 | - | OIL-400-EK-I-DW-3033 (Template-T2)
334 | SC-1 | 3 | 1 | 2 | 13 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[13].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-53-JBA-1101 | 17 | 18 | MC-1 | FRONT | EK-53-JBA-1101 | +17 | -18 | - | Spare
335 | SC-1 | 3 | 1 | 2 | 14 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[14].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | EK-53-JBA-1101 | 19 | 20 | MC-1 | FRONT | EK-53-JBA-1101 | +19 | -20 | - | Spare
336 | SC-1 | 3 | 1 | 2 | 15 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[15].Value | Proximity Switch | EK-53-ZSO-4703 | EK_ZSO_4703_53 | RO inlet | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-12 | +1 | -3 | MC-1 | FRONT | EK-53-JBN-1101 | 15 | 16 | MC-1 | FRONT | EK-53-JBN-1101 | +15 | -16 | - | OIL-400-EK-I-DW-3033 (Template-T1)
337 | SC-1 | 3 | 1 | 2 | 16 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[16].Value | Proximity Switch | EK-53-ZSC-4703 | EK_ZSC_4703_53 | RO inlet | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-12 | +4 | -6 | MC-1 | FRONT | EK-53-JBN-1101 | 17 | 18 | MC-1 | FRONT | EK-53-JBN-1101 | +17 | -18 | - | OIL-400-EK-I-DW-3033 (Template-T1)
338 | SC-1 | 3 | 1 | 2 | 17 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[17].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-16 | +1 | -3 | MC-1 | FRONT | EK-53-JBN-1101 | 19 | 20 | MC-1 | FRONT | EK-53-JBN-1101 | +19 | -20 | - | Spare
339 | SC-1 | 3 | 1 | 2 | 18 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[18].Value | Spare | Spare | Spare | Spare | Discrete | - | DI | Proximity Input | KFD2-SR2-EX2.W | D-16 | +4 | -6 | MC-1 | FRONT | EK-53-JBN-1101 | 21 | 22 | MC-1 | FRONT | EK-53-JBN-1101 | +21 | -22 | - | Spare
340 | SC-1 | 3 | 1 | 2 | 19 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[19].Value | ESD System relay Contact | EK-ESD-1 | EK_ESD_1 | Emergancy System Shutdown-1 | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Spare
341 | SC-1 | 3 | 1 | 2 | 20 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[20].Value | ESD System relay Contact | EK-ESD-2 | EK_ESD_2 | Emergancy System Shutdown-2 | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Spare
342 | SC-1 | 3 | 1 | 2 | 21 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[21].Value | - | EK-BPS-1-FAIL | EK_BPS_1_FAIL | Feeder System-1 Failuer | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T12)
343 | SC-1 | 3 | 1 | 2 | 22 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[22].Value | - | EK-BPS-2-FAIL | EK_BPS_2_FAIL | Feeder System-2 Failuer | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T12)
344 | SC-1 | 3 | 1 | 2 | 23 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[23].Value | - | EK-BPS-3-FAIL | EK_BPS_3_FAIL | Feeder System-3 Failuer | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T12)
345 | SC-1 | 3 | 1 | 2 | 24 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[24].Value | - | EK-FAN-1-FAIL | EK_FAN_1_FAIL | Fan Failure -1 | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T10)
346 | SC-1 | 3 | 1 | 2 | 25 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[25].Value | - | EK-FAN-2-FAIL | EK_FAN_2_FAIL | Fan Failure -2 | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T10)
347 | SC-1 | 3 | 1 | 2 | 26 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[26].Value | - | EK-FAN-3-FAIL | EK_FAN_3_FAIL | Fan Failure -3 | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T10)
348 | SC-1 | 3 | 1 | 2 | 27 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[27].Value | - | EK-UPS-FAIL | EK_UPS_FAIL | UPS Failure | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T9)
349 | SC-1 | 3 | 1 | 2 | 28 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[28].Value | - | EK-Temperature-High-1 | EK_Temperature_High_1 | Temperature High Alarm 1 | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T13)
350 | SC-1 | 3 | 1 | 2 | 29 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[29].Value | - | EK-Temperature-High-2 | EK_Temperature_High_2 | Temperature High Alarm 2 | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T13)
351 | SC-1 | 3 | 1 | 2 | 30 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[30].Value | - | EK-Temperature-High-3 | EK_Temperature_High_3 | Temperature High Alarm 3 | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T13)
352 | SC-1 | 3 | 1 | 2 | 31 | BMXDDI3202K | EIO2_d3_r1_s1_DI10.DIs_CH_IN[31].Value | - | EK-PS1-FAIL | EK_PS1_FAIL | Bulk Power Supply Failure (1&2) | Discrete | - | DI | Contact Type ( Wet Contact -24VDC ) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T11)
Digital Output
1 | SC-1 | 1 | 0 | 7 | 0 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[0].Value | On-Off Valve | EK-66-SDV-6501 | EK_SDV_6501_66 | Inlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 1 | 2 | MC-1 | REAR | EK-66-JBS-1101 | +1 | -2 | - | OIL-400-EK-I-DW-3033 (Template-T5)
2 | SC-1 | 1 | 0 | 7 | 1 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[1].Value | On-Off Valve | EK-66-SDV-6502 | EK_SDV_6502_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 3 | 4 | MC-1 | REAR | EK-66-JBS-1101 | +3 | -4 | - | OIL-400-EK-I-DW-3033 (Template-T5)
3 | SC-1 | 1 | 0 | 7 | 2 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[2].Value | On-Off Valve | EK-66-SDV-6503 | EK_SDV_6503_66 | Inlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 5 | 6 | MC-1 | REAR | EK-66-JBS-1101 | +5 | -6 | - | OIL-400-EK-I-DW-3033 (Template-T5)
4 | SC-1 | 1 | 0 | 7 | 3 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[3].Value | On-Off Valve | EK-66-SDV-6504 | EK_SDV_6504_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 7 | 8 | MC-1 | REAR | EK-66-JBS-1101 | +7 | -8 | - | OIL-400-EK-I-DW-3033 (Template-T5)
5 | SC-1 | 1 | 0 | 7 | 4 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[4].Value | On-Off Valve | EK-66-SDV-6505 | EK_SDV_6505_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 9 | 10 | MC-1 | REAR | EK-66-JBS-1101 | +9 | -10 | - | OIL-400-EK-I-DW-3033 (Template-T5)
6 | SC-1 | 1 | 0 | 7 | 5 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[5].Value | On-Off Valve | EK-66-SDV-6506 | EK_SDV_6506_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 11 | 12 | MC-1 | REAR | EK-66-JBS-1101 | +11 | -12 | - | OIL-400-EK-I-DW-3033 (Template-T5)
7 | SC-1 | 1 | 0 | 7 | 6 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[6].Value | On-Off Valve | EK-66-SDV-6507 | EK_SDV_6507_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 13 | 14 | MC-1 | REAR | EK-66-JBS-1101 | +13 | -14 | - | OIL-400-EK-I-DW-3033 (Template-T5)
8 | SC-1 | 1 | 0 | 7 | 7 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[7].Value | On-Off Valve | EK-66-SDV-6508 | EK_SDV_6508_66 | Outlet Of Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 15 | 16 | MC-1 | REAR | EK-66-JBS-1101 | +15 | -16 | - | OIL-400-EK-I-DW-3033 (Template-T5)
9 | SC-1 | 1 | 0 | 7 | 8 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[8].Value | On-Off Valve | EK-66-SDV-6509 | EK_SDV_6509_66 | Air Scouring Inlet in Walnut Shell Filter (EK-MAJ-6511) | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 17 | 18 | MC-1 | REAR | EK-66-JBS-1101 | +17 | -18 | - | OIL-400-EK-I-DW-3033 (Template-T5)
10 | SC-1 | 1 | 0 | 7 | 9 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[9].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 19 | 20 | MC-1 | REAR | EK-66-JBS-1101 | +19 | -20 | - | Spare
11 | SC-1 | 1 | 0 | 7 | 10 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[10].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 21 | 22 | MC-1 | REAR | EK-66-JBS-1101 | +21 | -22 | - | Spare
12 | SC-1 | 1 | 0 | 7 | 11 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[11].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1101 | 23 | 24 | MC-1 | REAR | EK-66-JBS-1101 | +23 | -24 | - | Spare
13 | SC-1 | 1 | 0 | 7 | 12 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[12].Value | On-Off Valve | EK-66-SDV-6516 | EK_SDV_6516_66 | Suction of Microbubble Pump-A (EK-PBA-6509A) | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 1 | 2 | MC-1 | REAR | EK-66-JBS-1102 | +1 | -2 | - | OIL-400-EK-I-DW-3033 (Template-T5)
14 | SC-1 | 1 | 0 | 7 | 13 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[13].Value | On-Off Valve | EK-66-SDV-6517 | EK_SDV_6517_66 | Suction of Microbubble Pump-B (EK-PBA-6509B) | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 3 | 4 | MC-1 | REAR | EK-66-JBS-1102 | +3 | -4 | - | OIL-400-EK-I-DW-3033 (Template-T5)
15 | SC-1 | 1 | 0 | 7 | 14 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[14].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 5 | 6 | MC-1 | REAR | EK-66-JBS-1102 | +5 | -6 | - | Spare
16 | SC-1 | 1 | 0 | 7 | 15 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[15].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 7 | 8 | MC-1 | REAR | EK-66-JBS-1102 | +7 | -8 | - | Spare
17 | SC-1 | 1 | 0 | 7 | 16 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[16].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 9 | 10 | MC-1 | REAR | EK-66-JBS-1102 | +9 | -10 | - | Spare
18 | SC-1 | 1 | 0 | 7 | 17 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[17].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 11 | 12 | MC-1 | REAR | EK-66-JBS-1102 | +11 | -12 | - | Spare
19 | SC-1 | 1 | 0 | 7 | 18 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[18].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 13 | 14 | MC-1 | REAR | EK-66-JBS-1102 | +13 | -14 | - | Spare
20 | SC-1 | 1 | 0 | 7 | 19 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[19].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 15 | 16 | MC-1 | REAR | EK-66-JBS-1102 | +15 | -16 | - | Spare
21 | SC-1 | 1 | 0 | 7 | 20 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[20].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 17 | 18 | MC-1 | REAR | EK-66-JBS-1102 | +17 | -18 | - | Spare
22 | SC-1 | 1 | 0 | 7 | 21 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[21].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 19 | 20 | MC-1 | REAR | EK-66-JBS-1102 | +19 | -20 | - | Spare
23 | SC-1 | 1 | 0 | 7 | 22 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[22].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 21 | 22 | MC-1 | REAR | EK-66-JBS-1102 | +21 | -22 | - | Spare
24 | SC-1 | 1 | 0 | 7 | 23 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[23].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-66-JBS-1102 | 23 | 24 | MC-1 | REAR | EK-66-JBS-1102 | +23 | -24 | - | Spare
25 | SC-1 | 1 | 0 | 7 | 24 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[24].Value | Motor Start/Stop Command | EK-66-XCA-6506 | EK_XCA_6506_66 | Microbubble Generator Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
26 | SC-1 | 1 | 0 | 7 | 25 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[25].Value | Motor Start/Stop Command | EK-66-XCA-6507 | EK_XCA_6507_66 | Microbubble Generator Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
27 | SC-1 | 1 | 0 | 7 | 26 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[26].Value | Motor Start/Stop Command | EK-66-XCA-6508 | EK_XCA_6508_66 | Filter Feed Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 5 | 6 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
28 | SC-1 | 1 | 0 | 7 | 27 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[27].Value | Motor Start/Stop Command | EK-66-XCA-6509 | EK_XCA_6509_66 | Filter Feed Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 7 | 8 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
29 | SC-1 | 1 | 0 | 7 | 28 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[28].Value | Motor Stop Command | EK-66-XCB-6510 | EK_XCB_6510_66 | Coagulant Dosing Tank Agitator | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 9 | 10 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
30 | SC-1 | 1 | 0 | 7 | 29 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[29].Value | Motor Start/Stop Command | EK-66-XCA-6516 | EK_XCA_6516_66 | Air Scouring Blower-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 11 | 12 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
31 | SC-1 | 1 | 0 | 7 | 30 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[30].Value | Motor Start/Stop Command | EK-66-XCA-6517 | EK_XCA_6517_66 | Air Scouring Blower-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 13 | 14 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
32 | SC-1 | 1 | 0 | 7 | 31 | BMXDDO3202K | EIO2_d1_r0_s7_DO1.DIs_CH_OUT[31].Value | Motor Start/Stop Command | EK-66-XCA-6518 | EK_XCA_6518_66 | Clarified Water Disposal Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 15 | 16 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
33 | SC-1 | 1 | 0 | 8 | 0 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[0].Value | Motor Start/Stop Command | EK-66-XCA-6519 | EK_XCA_6519_66 | Clarified Water Disposal Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 17 | 18 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
34 | SC-1 | 1 | 0 | 8 | 1 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[1].Value | Motor Start/Stop Command | EK-66-XCA-6520 | EK_XCA_6520_66 | Clarified Water Disposal Pump-C | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 19 | 20 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
35 | SC-1 | 1 | 0 | 8 | 2 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[2].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
36 | SC-1 | 1 | 0 | 8 | 3 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[3].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-01 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
37 | SC-1 | 1 | 0 | 8 | 4 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[4].Value | Motor Start/Stop Command | EK-66-XCA-6521 | EK_XCA_6521_66 | Effluent Water Drain Transfer Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
38 | SC-1 | 1 | 0 | 8 | 5 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[5].Value | Motor Start/Stop Command | EK-66-XCA-6522 | EK_XCA_6522_66 | Effluent Water Drain Transfer Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
39 | SC-1 | 1 | 0 | 8 | 6 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[6].Value | Motor Start/Stop Command | EK-66-XCA-6523 | EK_XCA_6523_66 | Slop Oil Transfer Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 5 | 6 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
40 | SC-1 | 1 | 0 | 8 | 7 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[7].Value | Motor Start/Stop Command | EK-66-XCA-6524 | EK_XCA_6524_66 | Slop Oil Transfer Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 7 | 8 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
41 | SC-1 | 1 | 0 | 8 | 8 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[8].Value | Motor Start/Stop Command | EK-66-XCA-6525 | EK_XCA_6525_66 | Centrifuge Feed Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 9 | 10 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
42 | SC-1 | 1 | 0 | 8 | 9 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[9].Value | Motor Start/Stop Command | EK-66-XCA-6526 | EK_XCA_6526_66 | Centrifuge Feed Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 11 | 12 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
43 | SC-1 | 1 | 0 | 8 | 10 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[10].Value | Motor Stop Command | EK-66-XCB-6530 | EK_XCB_6530_66 | DWPE Dosign Tank Agitator | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 13 | 14 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
44 | SC-1 | 1 | 0 | 8 | 11 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[11].Value | Motor Start/Stop Command | EK-66-XCA-6531 | EK_XCA_6531_66 | Skim Oil transfer Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 15 | 16 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
45 | SC-1 | 1 | 0 | 8 | 12 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[12].Value | Motor Start/Stop Command | EK-66-XCA-6532 | EK_XCA_6532_66 | Skim Oil transfer Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 17 | 18 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
46 | SC-1 | 1 | 0 | 8 | 13 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[13].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 19 | 20 | MC-1 | REAR | - | - | - | - | Spare
47 | SC-1 | 1 | 0 | 8 | 14 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[14].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
48 | SC-1 | 1 | 0 | 8 | 15 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[15].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-02 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
49 | SC-1 | 1 | 0 | 8 | 16 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[16].Value | Motor Start/Stop Command | EK-66-XCA-6533 | EK_XCA_6533_66 | Off-Spec Effluent Transfer Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
50 | SC-1 | 1 | 0 | 8 | 17 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[17].Value | Motor Start/Stop Command | EK-66-XCA-6534 | EK_XCA_6534_66 | Off-Spec Effluent Transfer Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
51 | SC-1 | 1 | 0 | 8 | 18 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[18].Value | Motor Stop Command | EK-66-XCB-6537 | EK_XCB_6537_66 | Sewage Lift Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 5 | 6 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
52 | SC-1 | 1 | 0 | 8 | 19 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[19].Value | Motor Stop Command | EK-66-XCB-6538 | EK_XCB_6538_66 | Sewage Lift Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 7 | 8 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
53 | SC-1 | 1 | 0 | 8 | 20 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[20].Value | Motor Stop Command | EK-66-XCB-6539 | EK_XCB_6539_66 | Sludge Recyclic Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 9 | 10 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
54 | SC-1 | 1 | 0 | 8 | 21 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[21].Value | Motor Stop Command | EK-66-XCB-6540 | EK_XCB_6540_66 | Sludge Recyclic Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 11 | 12 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
55 | SC-1 | 1 | 0 | 8 | 22 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[22].Value | Motor Stop Command | EK-66-XCB-6541 | EK_XCB_6541_66 | Air Blower-A for Aeration Tank | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 13 | 14 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
56 | SC-1 | 1 | 0 | 8 | 23 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[23].Value | Motor Stop Command | EK-66-XCB-6542 | EK_XCB_6542_66 | Air Blower-B for Aeration Tank | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 15 | 16 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
57 | SC-1 | 1 | 0 | 8 | 24 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[24].Value | Motor Stop Command | EK-66-XCB-6543 | EK_XCB_6543_66 | Filter Feed Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 17 | 18 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
58 | SC-1 | 1 | 0 | 8 | 25 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[25].Value | Motor Stop Command | EK-66-XCB-6544 | EK_XCB_6544_66 | Filter Feed Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 19 | 20 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
59 | SC-1 | 1 | 0 | 8 | 26 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[26].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
60 | SC-1 | 1 | 0 | 8 | 27 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[27].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-03 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
61 | SC-1 | 1 | 0 | 8 | 28 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[28].Value | Motor Stop Command | EK-66-XCB-6547 | EK_XCB_6547_66 | Treated Water Transfer Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
62 | SC-1 | 1 | 0 | 8 | 29 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[29].Value | Motor Stop Command | EK-66-XCB-6548 | EK_XCB_6548_66 | Treated Water Transfer Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
63 | SC-1 | 1 | 0 | 8 | 30 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[30].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 5 | 6 | MC-1 | REAR | - | - | - | - | Spare
64 | SC-1 | 1 | 0 | 8 | 31 | BMXDDO3202K | EIO2_d1_r0_s8_DO2.DIs_CH_OUT[31].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 7 | 8 | MC-1 | REAR | - | - | - | - | Spare
65 | SC-1 | 3 | 0 | 5 | 0 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[0].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 9 | 10 | MC-1 | REAR | - | - | - | - | Spare
66 | SC-1 | 3 | 0 | 5 | 1 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[1].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 11 | 12 | MC-1 | REAR | - | - | - | - | Spare
67 | SC-1 | 3 | 0 | 5 | 2 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[2].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 13 | 14 | MC-1 | REAR | - | - | - | - | Spare
68 | SC-1 | 3 | 0 | 5 | 3 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[3].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 15 | 16 | MC-1 | REAR | - | - | - | - | Spare
69 | SC-1 | 3 | 0 | 5 | 4 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[4].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 17 | 18 | MC-1 | REAR | - | - | - | - | Spare
70 | SC-1 | 3 | 0 | 5 | 5 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[5].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 19 | 20 | MC-1 | REAR | - | - | - | - | Spare
71 | SC-1 | 3 | 0 | 5 | 6 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[6].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
72 | SC-1 | 3 | 0 | 5 | 7 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[7].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-66-MCC-DO-04 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
73 | SC-1 | 3 | 0 | 5 | 8 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[8].Value | On-Off Valve | EK-53-SDV-4703 | EK_SDV_4703_53 | RO inlet | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 1 | 2 | MC-1 | REAR | EK-53-JBS-1601 | +1 | -2 | - | OIL-400-EK-I-DW-3033 (Template-T5)
74 | SC-1 | 3 | 0 | 5 | 9 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[9].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 3 | 4 | MC-1 | REAR | EK-53-JBS-1601 | +3 | -4 | - | OIL-400-EK-I-DW-3033 (Template-T5)
75 | SC-1 | 3 | 0 | 5 | 10 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[10].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 5 | 6 | MC-1 | REAR | EK-53-JBS-1601 | +5 | -6 | - | OIL-400-EK-I-DW-3033 (Template-T5)
76 | SC-1 | 3 | 0 | 5 | 11 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[11].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 7 | 8 | MC-1 | REAR | EK-53-JBS-1601 | +7 | -8 | - | OIL-400-EK-I-DW-3033 (Template-T5)
77 | SC-1 | 3 | 0 | 5 | 12 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[12].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 9 | 10 | MC-1 | REAR | EK-53-JBS-1601 | +9 | -10 | - | OIL-400-EK-I-DW-3033 (Template-T5)
78 | SC-1 | 3 | 0 | 5 | 13 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[13].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 11 | 12 | MC-1 | REAR | EK-53-JBS-1601 | +11 | -12 | - | OIL-400-EK-I-DW-3033 (Template-T5)
79 | SC-1 | 3 | 0 | 5 | 14 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[14].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 13 | 14 | MC-1 | REAR | EK-53-JBS-1601 | +13 | -14 | - | OIL-400-EK-I-DW-3033 (Template-T5)
80 | SC-1 | 3 | 0 | 5 | 15 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[15].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 15 | 16 | MC-1 | REAR | EK-53-JBS-1601 | +15 | -16 | - | OIL-400-EK-I-DW-3033 (Template-T5)
81 | SC-1 | 3 | 0 | 5 | 16 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[16].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 17 | 18 | MC-1 | REAR | EK-53-JBS-1601 | +17 | -18 | - | OIL-400-EK-I-DW-3033 (Template-T5)
82 | SC-1 | 3 | 0 | 5 | 17 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[17].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 19 | 20 | MC-1 | REAR | EK-53-JBS-1601 | +19 | -20 | - | OIL-400-EK-I-DW-3033 (Template-T5)
83 | SC-1 | 3 | 0 | 5 | 18 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[18].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 21 | 22 | MC-1 | REAR | EK-53-JBS-1601 | +21 | -22 | - | OIL-400-EK-I-DW-3033 (Template-T5)
84 | SC-1 | 3 | 0 | 5 | 19 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[19].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | On-Off Commans -(Wet-24VDC) | - | - | - | - | - | - | EK-53-JBS-1601 | 23 | 24 | MC-1 | REAR | EK-53-JBS-1601 | +23 | -24 | - | OIL-400-EK-I-DW-3033 (Template-T5)
85 | SC-1 | 3 | 0 | 5 | 20 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[20].Value | Motor Start/Stop Command | EK-53-XCA-4711 | EK_XCA_4711_53 | RO High Pressure Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 1 | 2 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
86 | SC-1 | 3 | 0 | 5 | 21 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[21].Value | Motor Start/Stop Command | EK-53-XCA-4712 | EK_XCA_4712_53 | RO High Pressure Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 3 | 4 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
87 | SC-1 | 3 | 0 | 5 | 22 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[22].Value | Motor Start/Stop Command | EK-53-XCA-4714 | EK_XCA_4714_53 | Potable Water Pump-A | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 5 | 6 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
88 | SC-1 | 3 | 0 | 5 | 23 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[23].Value | Motor Start/Stop Command | EK-53-XCA-4715 | EK_XCA_4715_53 | Potable Water Pump-B | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 7 | 8 | MC-1 | REAR | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T7)
89 | SC-1 | 3 | 0 | 5 | 24 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[24].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 9 | 10 | MC-1 | REAR | - | - | - | - | Spare
90 | SC-1 | 3 | 0 | 5 | 25 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[25].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 11 | 12 | MC-1 | REAR | - | - | - | - | Spare
91 | SC-1 | 3 | 0 | 5 | 26 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[26].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 13 | 14 | MC-1 | REAR | - | - | - | - | Spare
92 | SC-1 | 3 | 0 | 5 | 27 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[27].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 15 | 16 | MC-1 | REAR | - | - | - | - | Spare
93 | SC-1 | 3 | 0 | 5 | 28 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[28].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 17 | 18 | MC-1 | REAR | - | - | - | - | Spare
94 | SC-1 | 3 | 0 | 5 | 29 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[29].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 19 | 20 | MC-1 | REAR | - | - | - | - | Spare
95 | SC-1 | 3 | 0 | 5 | 30 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[30].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 21 | 22 | MC-1 | REAR | - | - | - | - | Spare
96 | SC-1 | 3 | 0 | 5 | 31 | BMXDDO3202K | EIO2_d3_r0_s5_DO3.DIs_CH_OUT[31].Value | Spare | Spare | Spare | Spare | Discrete | - | DO | MCC- Motor Command ( Potential Free Contact ) | - | - | - | - | - | - | EK-53-MCC-DO-01 | 23 | 24 | MC-1 | REAR | - | - | - | - | Spare
Analog Input
1 | SC-1 | 1 | 0 | 3 | 0 | BMXAMI0800 | EIO2_d1_r0_S3_AI1.ANA_CH_IN[0].ANA.Value | Flow Transmitter-Orifice Type | EK-66-FT-6501 | EK_FT_6501_66 | Miicrobubble Generator Pumps discharge t (EKEZZ- 6509A/B) | Analog | m3/hr | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-1 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1101 | 3 | 4 | MC-1 | FRONT | EK-66-JBN-1101 | +3 | -4 | S | OIL-400-EK-I-DW-3033 (Template-T8)
2 | SC-1 | 1 | 0 | 3 | 1 | BMXAMI0800 | EIO2_d1_r0_S3_AI1.ANA_CH_IN[1].ANA.Value | Level Transmitter - Ultrasonic Type | EK-66-LT-6501 | EK_LT_6501_66 | Filter Feed Tank | Analog | Mtr | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-2 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1101 | 1 | 2 | MC-1 | FRONT | EK-66-JBN-1101 | +1 | -2 | S | OIL-400-EK-I-DW-3033 (Template-T4)
3 | SC-1 | 1 | 0 | 3 | 2 | BMXAMI0800 | EIO2_d1_r0_S3_AI1.ANA_CH_IN[2].ANA.Value | Flow Transmitter-Orifice Type | EK-66-FT-6502 | EK_FT_6502_66 | Discharge Line of Air Scouring Blower ( EKPZZ- 6512 A/B) | Analog | Nm3/hr | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-3 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1101 | 7 | 8 | MC-1 | FRONT | EK-66-JBN-1101 | +7 | -8 | S | OIL-400-EK-I-DW-3033 (Template-T8)
4 | SC-1 | 1 | 0 | 3 | 3 | BMXAMI0800 | EIO2_d1_r0_S3_AI1.ANA_CH_IN[3].ANA.Value | Flow Transmitter-Orifice Type | EK-66-FT-6503 | EK_FT_6503_66 | Outline of Wallnut shell filter (EK-MAJ-6511) | Analog | m3/hr | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-4 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1101 | 9 | 10 | MC-1 | FRONT | EK-66-JBN-1101 | +9 | -10 | S | OIL-400-EK-I-DW-3033 (Template-T8)
5 | SC-1 | 1 | 0 | 3 | 4 | BMXAMI0800 | EIO2_d1_r0_S3_AI1.ANA_CH_IN[4].ANA.Value | OIL Analyzer | EK-66-AT-6501 | EK_AT_6501_66 | Outline of Wallnut shell filter (EK-MAJ-6511) | Analog | PPM | AI | 4-20 mA | KFD2-STC4-EX1.24 | AI-5 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1103 | 1 | 2 | MC-1 | FRONT | EK-66-JBN-1103 | +1 | -2 | S | OIL-400-EK-I-DW-3033 (Template-T8)
6 | SC-1 | 1 | 0 | 3 | 5 | BMXAMI0800 | EIO2_d1_r0_S3_AI1.ANA_CH_IN[5].ANA.Value | Pressure Transmitter | EK-66-PT-6501A | EK_PT_6501A_66 | Discharge Of Clarified Water Disposal Pump-A ( EK-PBA- 6513A) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-6 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1101 | 9 | 10 | MC-1 | FRONT | EK-53-JBN-1101 | +9 | -10 | S | OIL-400-EK-I-DW-3033 (Template-T4)
7 | SC-1 | 1 | 0 | 3 | 6 | BMXAMI0800 | EIO2_d1_r0_S3_AI1.ANA_CH_IN[6].ANA.Value | Pressure Transmitter | EK-66-PT-6501B | EK_PT_6501B_66 | Discharge Of Clarified Water Disposal Pump-B ( EK-PBA- 6513B) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-7 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1101 | 11 | 12 | MC-1 | FRONT | EK-53-JBN-1101 | +11 | -12 | S | OIL-400-EK-I-DW-3033 (Template-T4)
8 | SC-1 | 1 | 0 | 3 | 7 | BMXAMI0800 | EIO2_d1_r0_S3_AI1.ANA_CH_IN[7].ANA.Value | Pressure Transmitter | EK-66-PT-6501C | EK_PT_6501C_66 | Discharge Of Clarified Water Disposal Pump-C ( EK-PBA- 6513C) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-8 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1101 | 13 | 14 | MC-1 | FRONT | EK-53-JBN-1101 | +13 | -14 | S | OIL-400-EK-I-DW-3033 (Template-T4)
9 | SC-1 | 1 | 0 | 4 | 0 | BMXAMI0800 | EIO2_d1_r0_s4_AI2.ANA_CH_IN[0].ANA.Value | Differential Pressure Transmiter | EK-66-PDT-6501 | EK_PDT_6501_66 | Across Wallnut shell filter (EK-MAJ-6511) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-9 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1101 | 5 | 6 | MC-1 | FRONT | EK-66-JBN-1101 | +5 | -6 | S | OIL-400-EK-I-DW-3033 (Template-T4)
10 | SC-1 | 1 | 0 | 4 | 1 | BMXAMI0800 | EIO2_d1_r0_s4_AI2.ANA_CH_IN[1].ANA.Value | Level Transmitter - Ultrasonic Type | EK-66-LT-6502 | EK_LT_6502_66 | Effluent Water Drain Collection Sump | Analog | Mtr | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-10 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1101 | 13 | 14 | MC-1 | FRONT | EK-66-JBN-1101 | +13 | -14 | S | OIL-400-EK-I-DW-3033 (Template-T4)
11 | SC-1 | 1 | 0 | 4 | 2 | BMXAMI0800 | EIO2_d1_r0_s4_AI2.ANA_CH_IN[2].ANA.Value | Level Transmitter - Ultrasonic Type | EK-66-LT-6503 | EK_LT_6503_66 | Recovery Crude Storage Tank | Analog | Mtr | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-11 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1101 | 15 | 16 | MC-1 | FRONT | EK-66-JBN-1101 | +15 | -16 | S | OIL-400-EK-I-DW-3033 (Template-T4)
12 | SC-1 | 1 | 0 | 4 | 3 | BMXAMI0800 | EIO2_d1_r0_s4_AI2.ANA_CH_IN[3].ANA.Value | Pressure Transmitter | EK-66-PT-650XA | EK_PT_6504A_66 | Discharge Of Slop Oil Transfer Pump-A(EK-PBA-6520A) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-12 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1102 | 13 | 14 | MC-1 | FRONT | EK-66-JBN-1102 | +13 | -14 | S | OIL-400-EK-I-DW-3033 (Template-T4)
13 | SC-1 | 1 | 0 | 4 | 4 | BMXAMI0800 | EIO2_d1_r0_s4_AI2.ANA_CH_IN[4].ANA.Value | Pressure Transmitter | EK-66-PT-650XB | EK_PT_6504B_66 | Discharge Of Slop Oil Transfer Pump-B(EK-PBA-6520B) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-13 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1102 | 15 | 16 | MC-1 | FRONT | EK-66-JBN-1102 | +15 | -16 | S | OIL-400-EK-I-DW-3033 (Template-T4)
14 | SC-1 | 1 | 0 | 4 | 5 | BMXAMI0800 | EIO2_d1_r0_s4_AI2.ANA_CH_IN[5].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AI | 4-20 mA | KFD2-STC4-EX1.33 | AI-14 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1102 | 17 | 18 | MC-1 | FRONT | EK-66-JBN-1102 | +17 | -18 | S | OIL-400-EK-I-DW-3033 (Template-T4)
15 | SC-1 | 1 | 0 | 4 | 6 | BMXAMI0800 | EIO2_d1_r0_s4_AI2.ANA_CH_IN[6].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-15 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1102 | 19 | 20 | MC-1 | FRONT | EK-66-JBN-1102 | +19 | -20 | S | OIL-400-EK-I-DW-3033 (Template-T4)
16 | SC-1 | 1 | 0 | 4 | 7 | BMXAMI0800 | EIO2_d1_r0_s4_AI2.ANA_CH_IN[7].ANA.Value | Flow Transmitter-Magnetic Type | EK-66-FT-6505 | EK_FT_6505_66 | Discharge Line of Slop Oil Transfer Pump (EK-PBA-6520A/B) | Analog | m3/hr | AI | 4-20 mA | KFD2-STC4-EX1.35 | AI-16 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1103 | 5 | 6 | MC-1 | FRONT | EK-66-JBN-1103 | +5 | -6 | S | OIL-400-EK-I-DW-3033 (Template-T8)
17 | SC-1 | 3 | 0 | 3 | 0 | BMXAMI0800 | EIO2_d3_r0_s3_AI3.ANA_CH_IN[0].ANA.Value | Level Transmitter - Ultrasonic Type | EK-66-LT-6504 | EK_LT_6504_66 | Sludge Sump | Analog | Mtr | AI | 4-20 mA | KFD2-STC4-EX1.36 | AI-17 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1101 | 17 | 18 | MC-1 | FRONT | EK-66-JBN-1101 | +17 | -18 | S | OIL-400-EK-I-DW-3033 (Template-T4)
18 | SC-1 | 3 | 0 | 3 | 1 | BMXAMI0800 | EIO2_d3_r0_s3_AI3.ANA_CH_IN[1].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AI | 4-20 mA | KFD2-STC4-EX1.37 | AI-18 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1101 | 19 | 20 | MC-1 | FRONT | EK-66-JBN-1101 | +19 | -20 | S | OIL-400-EK-I-DW-3033 (Template-T4)
19 | SC-1 | 3 | 0 | 3 | 2 | BMXAMI0800 | EIO2_d3_r0_s3_AI3.ANA_CH_IN[2].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AI | 4-20 mA | KFD2-STC4-EX1.38 | AI-19 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1101 | 21 | 22 | MC-1 | FRONT | EK-66-JBN-1101 | +21 | -22 | S | OIL-400-EK-I-DW-3033 (Template-T4)
20 | SC-1 | 3 | 0 | 3 | 3 | BMXAMI0800 | EIO2_d3_r0_s3_AI3.ANA_CH_IN[3].ANA.Value | Flow Transmitter-Magnetic Type | EK-66-FT-6504 | EK_FT_6504_66 | Discharge Line of Effluent Water Drain Transfer Pump (EK-PBA-6522A/B) | Analog | m3/hr | AI | 4-20 mA | KFD2-STC4-EX1.35 | AI-16 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1103 | 3 | 4 | MC-1 | FRONT | EK-66-JBN-1103 | +3 | -4 | S | OIL-400-EK-I-DW-3033 (Template-T8)
21 | SC-1 | 3 | 0 | 3 | 4 | BMXAMI0800 | EIO2_d3_r0_s3_AI3.ANA_CH_IN[4].ANA.Value | Flow Transmitter-Magnetic Type | EK-66-FT-6506 | EK_FT_6506_66 | Discharge Line of CentrifugeFeed Pump (EK-PBA-6517A/B) | Analog | m3/hr | AI | 4-20 mA | KFD2-STC4-EX1.36 | AI-17 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1103 | 7 | 8 | MC-1 | FRONT | EK-66-JBN-1103 | +7 | -8 | S | OIL-400-EK-I-DW-3033 (Template-T8)
22 | SC-1 | 3 | 0 | 3 | 5 | BMXAMI0800 | EIO2_d3_r0_s3_AI3.ANA_CH_IN[5].ANA.Value | Flow Transmitter-Magnetic Type | EK-66-FT-6508 | EK_FT_6508_66 | Discharge Line of Skim Oil Transfer Pump (EK-PBA-6515A/B) | Analog | m3/hr | AI | 4-20 mA | KFD2-STC4-EX1.37 | AI-18 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1103 | 11 | 12 | MC-1 | FRONT | EK-66-JBN-1103 | +11 | -12 | S | OIL-400-EK-I-DW-3033 (Template-T8)
23 | SC-1 | 3 | 0 | 3 | 6 | BMXAMI0800 | EIO2_d3_r0_s3_AI3.ANA_CH_IN[6].ANA.Value | Flow Transmitter-Magnetic Type | EK-66-FT-6507 | EK_FT_6507_66 | Discharge Line of Off Spec Effluent Water Transfer Pump (EK-PBA-6514A/B) | Analog | m3/hr | AI | 4-20 mA | KFD2-STC4-EX1.38 | AI-19 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1103 | 13 | 14 | MC-1 | FRONT | EK-66-JBN-1103 | +13 | -14 | S | OIL-400-EK-I-DW-3033 (Template-T8)
24 | SC-1 | 3 | 0 | 3 | 7 | BMXAMI0800 | EIO2_d3_r0_s3_AI3.ANA_CH_IN[7].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-20 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1103 | 15 | 16 | MC-1 | FRONT | EK-66-JBN-1103 | +15 | -16 | S | OIL-400-EK-I-DW-3033 (Template-T4)
25 | SC-1 | 3 | 0 | 4 | 0 | BMXAMI0800 | EIO2_d3_r0_s4_AI4.ANA_CH_IN[0].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-21 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1103 | 17 | 18 | MC-1 | FRONT | EK-66-JBN-1103 | +17 | -18 | S | OIL-400-EK-I-DW-3033 (Template-T4)
26 | SC-1 | 3 | 0 | 4 | 1 | BMXAMI0800 | EIO2_d3_r0_s4_AI4.ANA_CH_IN[1].ANA.Value | Pressure Transmitter | EK-66-PT-6502A | EK_PT_6502A_66 | Discharge Line of Off Spec Effluent Water Transfer Pump-A (EK-PBA-6514A) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-22 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1102 | 3 | 4 | MC-1 | FRONT | EK-66-JBN-1102 | +3 | -4 | S | OIL-400-EK-I-DW-3033 (Template-T4)
27 | SC-1 | 3 | 0 | 4 | 2 | BMXAMI0800 | EIO2_d3_r0_s4_AI4.ANA_CH_IN[2].ANA.Value | Pressure Transmitter | EK-66-PT-6502B | EK_PT_6502B_66 | Discharge Line of Off Spec Effluent Water Transfer Pump-B (EK-PBA-6514B) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-23 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1102 | 5 | 6 | MC-1 | FRONT | EK-66-JBN-1102 | +5 | -6 | S | OIL-400-EK-I-DW-3033 (Template-T4)
28 | SC-1 | 3 | 0 | 4 | 3 | BMXAMI0800 | EIO2_d3_r0_s4_AI4.ANA_CH_IN[3].ANA.Value | Pressure Transmitter | EK-66-PT-6503A | EK_PT_6503A_66 | Discharge Line of Skim Oil Transfer Pump-A (EK-PBA-6515A) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-24 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1102 | 9 | 10 | MC-1 | FRONT | EK-66-JBN-1102 | +9 | -10 | S | OIL-400-EK-I-DW-3033 (Template-T4)
29 | SC-1 | 3 | 0 | 4 | 4 | BMXAMI0800 | EIO2_d3_r0_s4_AI4.ANA_CH_IN[4].ANA.Value | Pressure Transmitter | EK-66-PT-6503B | EK_PT_6503B_66 | Discharge Line of Skim Oil Transfer Pump-B (EK-PBA-6515B) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-25 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1102 | 11 | 12 | MC-1 | FRONT | EK-66-JBN-1102 | +11 | -12 | S | OIL-400-EK-I-DW-3033 (Template-T4)
30 | SC-1 | 3 | 0 | 4 | 5 | BMXAMI0800 | EIO2_d3_r0_s4_AI4.ANA_CH_IN[5].ANA.Value | Flow Transmitter-Orifice Type | EK-53-FT-4701 | EK_FT_4701_53 | Discharge Of Deep Well Pump (EK-PBS-4701A/B/C) | Analog | m3/hr | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-26 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1101 | 5 | 6 | MC-1 | FRONT | EK-53-JBN-1101 | +5 | -6 | S | OIL-400-EK-I-DW-3033 (Template-T8)
31 | SC-1 | 3 | 0 | 4 | 6 | BMXAMI0800 | EIO2_d3_r0_s4_AI4.ANA_CH_IN[6].ANA.Value | Differential Pressure Transmiter | EK-53-PDT-4701A | EK_PDI_4701A_53 | Across of Iron Removal Filter-A (EK-MAJ-4704A) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-27 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1101 | 1 | 2 | MC-1 | FRONT | EK-53-JBN-1101 | +1 | -2 | S | OIL-400-EK-I-DW-3033 (Template-T4)
32 | SC-1 | 3 | 0 | 4 | 7 | BMXAMI0800 | EIO2_d3_r0_s4_AI4.ANA_CH_IN[7].ANA.Value | Differential Pressure Transmiter | EK-53-PDT-4701B | EK_PDI_4701B_53 | Across of Iron Removal Filter-B (EK-MAJ-4704B) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-28 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1101 | 3 | 4 | MC-1 | FRONT | EK-53-JBN-1101 | +3 | -4 | S | OIL-400-EK-I-DW-3033 (Template-T4)
33 | SC-1 | 3 | 1 | 4 | 0 | BMXAMI0800 | EIO2_d3_r1_s3_AI5.ANA_CH_IN[0].ANA.Value | pH Analyzer | EK-53-AT-4704 | EK_AT_4704_53 | pH analyzer at RO inlet | Analog | pH | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-29 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | 13 | 14 | MC-1 | FRONT | EK-53-JBN-1102 | +13 | -14 | S | OIL-400-EK-I-DW-3033 (Template-T8)
34 | SC-1 | 3 | 1 | 4 | 1 | BMXAMI0800 | EIO2_d3_r1_s3_AI5.ANA_CH_IN[1].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-28 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | 15 | 16 | MC-1 | FRONT | EK-53-JBN-1102 | +15 | -16 | S | OIL-400-EK-I-DW-3033 (Template-T4)
35 | SC-1 | 3 | 1 | 4 | 2 | BMXAMI0800 | EIO2_d3_r1_s3_AI5.ANA_CH_IN[2].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-29 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | 17 | 18 | MC-1 | FRONT | EK-53-JBN-1102 | +17 | -18 | S | OIL-400-EK-I-DW-3033 (Template-T4)
36 | SC-1 | 3 | 1 | 4 | 3 | BMXAMI0800 | EIO2_d3_r1_s3_AI5.ANA_CH_IN[3].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-30 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | 19 | 20 | MC-1 | FRONT | EK-53-JBN-1102 | +19 | -20 | S | OIL-400-EK-I-DW-3033 (Template-T4)
37 | SC-1 | 3 | 1 | 4 | 4 | BMXAMI0800 | EIO2_d3_r1_s3_AI5.ANA_CH_IN[4].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AI | 4-20 mA | KFD2-STC4-EX1.50 | AI-31 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | 21 | 22 | MC-1 | FRONT | EK-53-JBN-1102 | +21 | -22 | S | OIL-400-EK-I-DW-3033 (Template-T4)
38 | SC-1 | 3 | 1 | 4 | 5 | BMXAMI0800 | EIO2_d3_r1_s3_AI5.ANA_CH_IN[5].ANA.Value | ORP Analyzer | EK-53-AT-4701 | EK_AT_4701_53 | pH analyzer at RO inlet | Analog | mV | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-32 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | 7 | 8 | MC-1 | FRONT | EK-53-JBN-1102 | +7 | -8 | S | OIL-400-EK-I-DW-3033 (Template-T8)
39 | SC-1 | 3 | 1 | 4 | 6 | BMXAMI0800 | EIO2_d3_r1_s3_AI5.ANA_CH_IN[6].ANA.Value | Flow Transmitter-Orifice Type | EK-53-FT-4702 | EK_FT_4702_53 | RO High Pressure Pump Outlet (EK-PBA-4707A/B) | Analog | m3/hr | AI | 4-20 mA | KFD2-STC4-EX1.52 | AI-33 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | 1 | 2 | MC-1 | FRONT | EK-53-JBN-1102 | +1 | -2 | S | OIL-400-EK-I-DW-3033 (Template-T8)
40 | SC-1 | 3 | 1 | 4 | 7 | BMXAMI0800 | EIO2_d3_r1_s3_AI5.ANA_CH_IN[7].ANA.Value | pH Analyzer | EK-53-AT-4702A | EK_AT_4702A_53 | RO-A Skid Outlet (EK-ZZZ-4708A) | Analog | pH | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-34 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | 9 | 10 | MC-1 | FRONT | EK-53-JBN-1102 | +9 | -10 | S | OIL-400-EK-I-DW-3033 (Template-T8)
41 | SC-1 | 3 | 1 | 5 | 0 | BMXAMI0800 | EIO2_d3_r1_s4_AI5.ANA_CH_IN[0].ANA.Value | pH Analyzer | EK-53-AT-4702B | EK_AT_4702B_53 | RO-B Skid Outlet (EK-ZZZ-4708B) | Analog | pH | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-35 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | - | - | MC-1 | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T8)
42 | SC-1 | 3 | 1 | 5 | 1 | BMXAMI0800 | EIO2_d3_r1_s4_AI5.ANA_CH_IN[1].ANA.Value | Conductivity Analyzer | EK-53-AT-4703A | EK_AT_4703A_53 | RO-A Skid Outlet (EK-ZZZ-4708A) | Analog | μs/cm | AI | 4-20 mA | KFD2-STC4-EX1.55 | AI-36 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | 11 | 12 | MC-1 | FRONT | EK-53-JBN-1102 | +11 | -12 | S | OIL-400-EK-I-DW-3033 (Template-T8)
43 | SC-1 | 3 | 1 | 5 | 2 | BMXAMI0800 | EIO2_d3_r1_s4_AI5.ANA_CH_IN[2].ANA.Value | Conductivity Analyzer | EK-53-AT-4703B | EK_AT_4703B_53 | RO-B Skid Outlet (EK-ZZZ-4708B) | Analog | μs/cm | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-37 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | - | - | MC-1 | - | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T8)
44 | SC-1 | 3 | 1 | 5 | 3 | BMXAMI0800 | EIO2_d3_r1_s4_AI5.ANA_CH_IN[3].ANA.Value | Differential Pressure Transmiter | EK-53-PDT-4702A | EK_PDT_4702A_53 | Across RO-A Skid Outlet (EK-ZZZ-4708A) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-38 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | 3 | 4 | MC-1 | FRONT | EK-53-JBN-1102 | +3 | -4 | S | OIL-400-EK-I-DW-3033 (Template-T4)
45 | SC-1 | 3 | 1 | 5 | 4 | BMXAMI0800 | EIO2_d3_r1_s4_AI5.ANA_CH_IN[4].ANA.Value | Differential Pressure Transmiter | EK-53-PDT-4702B | EK_PDT_4702B_53 | Across RO-B Skid Outlet (EK-ZZZ-4708B) | Analog | Kg/cm2 | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-39 | 1(+) | 3(-) | MC-1 | FRONT | EK-53-JBN-1102 | 5 | 6 | MC-1 | FRONT | EK-53-JBN-1102 | +5 | -6 | S | OIL-400-EK-I-DW-3033 (Template-T4)
46 | SC-1 | 3 | 1 | 5 | 5 | BMXAMI0800 | EIO2_d3_r1_s4_AI5.ANA_CH_IN[5].ANA.Value | Flow Transmitter-Magnetic Type | EK-66-FT-6509 | EK_FT_6509_66 | Discharge of Sewage Lift Pump (EK-PBA-6335A/B) | Analog | m3/hr | AI | 4-20 mA | KFD2-STC4-EX1.55 | AI-40 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1103 | 9 | 10 | MC-1 | FRONT | EK-66-JBN-1103 | +9 | -10 | S | OIL-400-EK-I-DW-3033 (Template-T8)
47 | SC-1 | 3 | 1 | 5 | 6 | BMXAMI0800 | EIO2_d3_r1_s4_AI5.ANA_CH_IN[6].ANA.Value | Flow Transmitter-Orifice Type | EK-66-FT-6510 | EK_FT_6510_66 | Discharge Of Treated Water Transfer Pump(EK-ABJ-6543A/B) | Analog | m3/hr | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-41 | 1(+) | 3(-) | MC-1 | FRONT | EK-66-JBN-1101 | 11 | 12 | MC-1 | FRONT | EK-66-JBN-1101 | +11 | -12 | S | OIL-400-EK-I-DW-3033 (Template-T8)
48 | SC-1 | 3 | 1 | 5 | 7 | BMXAMI0800 | EIO2_d3_r1_s4_AI5.ANA_CH_IN[7].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AI | 4-20 mA | KFD2-STC4-EX1.20 | AI-42 | 1(+) | 3(-) | MC-1 | FRONT | Spare | Spare | Spare | MC-1 | FRONT | - | - | - | - | OIL-400-EK-I-DW-3033 (Template-T4)
Analog Output
1 | SC-1 | 1 | 0 | 5 | 0 | BMXAMO0802 | EIO2_d1_r0_s5_AO1.ANA_CH_OUT[0].ANA.Value | Control Valve | EK-66-FV-6515 | EK_FV_6515_66 | Skim Oil | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-1 | 1(+) | 2(-) | MC-1 | FRONT | EK-66-JBN-1102 | 7 | 8 | MC-1 | FRONT | EK-66-JBN-1102 | +7 | -8 | S | OIL-400-EK-I-DW-3033 (Template-T6)
2 | SC-1 | 1 | 0 | 5 | 1 | BMXAMO0802 | EIO2_d1_r0_s5_AO1.ANA_CH_OUT[1].ANA.Value | Control Valve | EK-66-FV-6514 | EK_FV_6514_66 | Effluent Water | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-2 | 1(+) | 2(-) | MC-1 | FRONT | EK-66-JBN-1102 | 1 | 2 | MC-1 | FRONT | EK-66-JBN-1102 | +1 | -2 | S | OIL-400-EK-I-DW-3033 (Template-T6)
3 | SC-1 | 1 | 0 | 5 | 2 | BMXAMO0802 | EIO2_d1_r0_s5_AO1.ANA_CH_OUT[2].ANA.Value | Control Valve | EK-53-FV-4701 | EK_FV_4701_53 | Discharge Of Deep Well Pump (EK-PBS-4701A/B/C) | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-3 | 1(+) | 2(-) | MC-1 | FRONT | EK-53-JBN-1101 | 7 | 8 | MC-1 | FRONT | EK-53-JBN-1101 | +7 | -8 | S | OIL-400-EK-I-DW-3033 (Template-T6)
4 | SC-1 | 1 | 0 | 5 | 3 | BMXAMO0802 | EIO2_d1_r0_s5_AO1.ANA_CH_OUT[3].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-4 | 1(+) | 2(-) | MC-1 | FRONT | EK-66-JBN-1102 | 23 | 24 | MC-1 | FRONT | EK-66-JBN-1102 | 23 | 24 | S | OIL-400-EK-I-DW-3033 (Template-T6)
5 | SC-1 | 1 | 0 | 5 | 4 | BMXAMO0802 | EIO2_d1_r0_s5_AO1.ANA_CH_OUT[4].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-5 | 1(+) | 2(-) | MC-1 | FRONT | EK-53-JBN-1101 | 15 | 16 | MC-1 | FRONT | EK-53-JBN-1101 | +15 | -16 | S | OIL-400-EK-I-DW-3033 (Template-T6)
6 | SC-1 | 1 | 0 | 5 | 5 | BMXAMO0802 | EIO2_d1_r0_s5_AO1.ANA_CH_OUT[5].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-6 | 1(+) | 2(-) | MC-1 | FRONT | EK-53-JBN-1101 | 17 | 18 | MC-1 | FRONT | EK-53-JBN-1101 | +17 | -18 | S | OIL-400-EK-I-DW-3033 (Template-T6)
7 | SC-1 | 1 | 0 | 5 | 6 | BMXAMO0802 | EIO2_d1_r0_s5_AO1.ANA_CH_OUT[6].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-7 | 1(+) | 2(-) | MC-1 | FRONT | EK-53-JBN-1101 | 19 | 20 | MC-1 | FRONT | EK-53-JBN-1101 | +19 | -20 | S | OIL-400-EK-I-DW-3033 (Template-T6)
8 | SC-1 | 1 | 0 | 5 | 7 | BMXAMO0802 | EIO2_d1_r0_s5_AO1.ANA_CH_OUT[7].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-8 | 1(+) | 2(-) | MC-1 | FRONT | Spare-AO | 1 | 2 | MC-1 | FRONT | - | - | - | - | Spare
9 | SC-1 | 1 | 0 | 6 | 0 | BMXAMO0802 | EIO2_d1_r0_s6_AO2.ANA_CH_OUT[0].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-9 | 1(+) | 2(-) | MC-1 | FRONT | Spare-AO | 3 | 4 | MC-1 | FRONT | - | - | - | - | Spare
10 | SC-1 | 1 | 0 | 6 | 1 | BMXAMO0802 | EIO2_d1_r0_s6_AO2.ANA_CH_OUT[1].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-10 | 1(+) | 2(-) | MC-1 | FRONT | Spare-AO | 5 | 6 | MC-1 | FRONT | - | - | - | - | Spare
11 | SC-1 | 1 | 0 | 6 | 2 | BMXAMO0802 | EIO2_d1_r0_s6_AO2.ANA_CH_OUT[2].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-11 | 1(+) | 2(-) | MC-1 | FRONT | Spare-AO | 7 | 8 | MC-1 | FRONT | - | - | - | - | Spare
12 | SC-1 | 1 | 0 | 6 | 3 | BMXAMO0802 | EIO2_d1_r0_s6_AO2.ANA_CH_OUT[3].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-12 | 1(+) | 2(-) | MC-1 | FRONT | Spare-AO | 9 | 10 | MC-1 | FRONT | - | - | - | - | Spare
13 | SC-1 | 1 | 0 | 6 | 4 | BMXAMO0802 | EIO2_d1_r0_s6_AO2.ANA_CH_OUT[4].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-13 | 1(+) | 2(-) | MC-1 | FRONT | Spare-AO | 11 | 12 | MC-1 | FRONT | - | - | - | - | Spare
14 | SC-1 | 1 | 0 | 6 | 5 | BMXAMO0802 | EIO2_d1_r0_s6_AO2.ANA_CH_OUT[5].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-14 | 1(+) | 2(-) | MC-1 | FRONT | Spare-AO | 13 | 14 | MC-1 | FRONT | - | - | - | - | Spare
15 | SC-1 | 1 | 0 | 6 | 6 | BMXAMO0802 | EIO2_d1_r0_s6_AO2.ANA_CH_OUT[6].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-15 | 1(+) | 2(-) | MC-1 | FRONT | Spare-AO | 15 | 16 | MC-1 | FRONT | - | - | - | - | Spare
16 | SC-1 | 1 | 0 | 6 | 7 | BMXAMO0802 | EIO2_d1_r0_s6_AO2.ANA_CH_OUT[7].ANA.Value | Spare | Spare | Spare | Spare | Analog | - | AO | 4-20 mA | KFD2-SCD-Ex1 | AO-16 | 1(+) | 2(-) | MC-1 | FRONT | Spare-AO | 17 | 18 | MC-1 | FRONT | - | - | - | - | Spare

## Comment
Comment
a) Include loop Number in IO assignment .
b) Do normal colour of yellow coloured block while submission of Document.
c) Bulk power supply failure alarm indication are missing include same.
d) Feel all cloumn for spare , as spare.
e) Submit final PDF copy of IO assignment along with Excel copy in next revision.
f) Include Abbreviation & Notes sheet in this document.
g) It may be noted that in pdf copy all column words should be clearly readable.
ABBREVIATION