## Register List
Category | Sub Cat 1 | Sub Cat 2 | Description | PM1125H | PM2105H | EM6459H | DM6200H | EM6433H | EM6436H | PM1120H | EM6438H | PM1130H | Register | Units | Size (INT16) | Data Type | Access EM64xxH_PM11XXH | Range | Default | User Notes | Developer Notes
| Product & Features |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 30 | --- |  | --- | --- | --- | ---
|  |  | Meter Name | Y | Y | Y | Y | Y | Y | Y | Y | Y | 30 | --- | 20 | UTF8 | RWC | --- | PM5xxx = "Power Meter"
|  |  | Meter Model | Y | Y | Y | Y | Y | Y | Y | Y | Y | 50 | --- | 20 | UTF8 | RWC | --- | EM6459HNC = "EM6459H" EM6459H = "EM6459H" DM6200H = "DM6200H" EM6433H = "EM6433H" EM6436HNC = "EM6436H" EM6436H = "EM6436H" PM1120H = "PM1120H" PM1130H = "PM1130H" DM6000 = "DM6000"
|  |  | Manufacturer | Y | Y | Y | Y | Y | Y | Y | Y | Y | 70 | --- | 20 | UTF8 | RWC | --- | "Schneider Electric"
|  |  | Product ID Number | Y | Y | Y | Y | Y | Y | Y | Y | Y | 90 | --- | 1 | INT16U | RWC |  | EM6459HNC = 15535 EM6459H = 15536 DM6200H = 15537 EM6433H = 15538 EM6436HNC = 15539 EM6436H = 15540 Em6438H = 15541 PM1120H = 15542 PM1130H = 15543 DM6000H = 15544
|  |  | Hardware Detected | Y | Y | Y | Y | Y | Y | Y | Y | Y | 91 | --- | 4 | BITMAP | R | 0x0000 – 0xFFFF | EM6459HNC = 0x0003 EM6459H = 0x0003 DM6000H = 0x0003 DM6200H = 0x0003 EM6433H = 0x0003 EM6436H = 0x0003 EM6438H = 0x0003 PM1120H = 0x0003 PM1130H = 0x0003 | Bitmap indicating base hardware options detected Bit 01 = HMI Bit 02 = Modbus Serial Communications Port Bit 03 = Modbus Ethernet Communications Port Bit 04 = Digital Inputs Bit 05 = Digital Outputs Bit 06-16 Not Used
|  |  | Supported Features | Y | Y | Y | Y | Y | Y | Y | Y | Y | 95 | --- | 4 | BITMAP | R | 0x0000 – 0xFFFF | EM6459HNC = 0x0003 EM6459H = 0x0003 DM6000H = 0x0003 DM6200H = 0x0003 EM6433H = 0x0015 EM6436H = 0x0015 EM6438H = 0x0015 PM1120H = 0x0215 PM1130H = 0x0215 | Bitmap indicating features supported Bit 01 = 1 Cycle Metering Bit 02 = 5/6 Cycle Metering Bit 03 = 50/60 Cycle Metering Bit 04 = Min/Max Bit 05 = Accumulated Energy Bit 06 = Conditional Energy Bit 07 = Time-of-Use Energy Bit 08 = Multi-tarrif Energy Bit 09 = Input Metering Bit 10 = Demand Bit 11 = Alarms Bit 12 = Waveform Capture Bit 13 = Datalogging Bit 14 = Not Used Bit 15 = Not Used Bit 16 = Not Used
| Manufacturing Data |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 116 | --- |  | --- | --- | --- | ---
|  | Meter |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 116 | --- |  | --- | --- | --- | ---
|  |  | Production Track Id | H | H | H | H | H | H | H | H | H |  |  | 1 | INT16U | R | --- | 0 | Production Track ID
|  |  | ASCII Serial Number | R | R | R | R | R | R | R | R | R | 117 | --- | 12 | UTF8 |  | --- | 0 | ION Serial Number, in ASCII | Added for ION meters which require an ASCII serial number.
|  |  | Manufacturing Unit Id | Y | Y | Y | Y | Y | Y | Y | Y | Y | 129 |  | 1 | INT16U | R | --- | 0 | Manufacturing Unit ID | (To be prefixed in Serial Number While Displaying)
|  |  | Serial Number | Y | Y | Y | Y | Y | Y | Y | Y | Y | 130 | --- | 2 | INT32U | R | --- | 0 |  | UTF8 in ION meters
|  |  | Date of Manufacture | Y | Y | Y | Y | Y | Y | Y | Y | Y | 132 | --- | 4 | DATETIME | R | --- | 0
|  |  | Hardware Revision | Y | Y | Y | Y | Y | Y | Y | Y | Y | 136 | --- | 5 | UTF8 | R | --- | 0
|  |  | Production History 01 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 141 | --- | 1 | INT16U | R | --- | 0 |  | This is encoded into a packed binary format
|  |  | Production History 02 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 142 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 03 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 143 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 04 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 144 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 05 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 145 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 06 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 146 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 07 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 147 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 08 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 148 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 09 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 149 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 10 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 150 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 11 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 151 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 12 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 152 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 13 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 153 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 14 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 154 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 15 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 155 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 16 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 156 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 17 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 157 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 18 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 158 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 19 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 159 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 20 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 160 | --- | 1 | INT16U | R | --- | 0
|  |  | Checksum | Y | Y | Y | Y | Y | Y | Y | Y | Y | 161 | --- | 1 | INT16U | R | --- | 0
| Firmware Versions |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1637 | --- |  | --- | --- | --- | ---
|  | Operating System |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1637 | --- |  | --- | --- | --- | ---
|  |  | Present Firmware Version (DLF Format) X.Y.T | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1637 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | The firmware version takes the following form: XXYYT | UTF8 in ION meters
|  |  | X – Major | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1638 | --- | 1 | INT16U | R | 00 – 99 | 0
|  |  | Y – Minor | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1639 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Z – Quality | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1640 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | T – Internal evolutions | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1641 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Previous Firmware Version (DLF Format) X.Y.T | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1642 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | The firmware version takes the following form: XXYYT
|  |  | X – Major | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1643 | --- | 1 | INT16U | R | 00 – 99 | 0
|  |  | Y – Minor | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1644 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Z – Quality | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1645 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | T – Internal evolutions | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1646 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  | Reset |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1669 | --- |  | --- | --- | --- | ---
|  |  | Present Firmware Version (DLF Format) X.Y.T | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1669 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | The firmware version takes the following form: XXYYT
|  |  | X – Major | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1670 | --- | 1 | INT16U | R | 00 – 99 | 0
|  |  | Y – Minor | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1671 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Z – Quality | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1672 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | T – Internal evolutions | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1673 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Previous Firmware Version (DLF Format) X.Y.T | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1674 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | Not supported in PM5xxx. Space reserved to preserve NVRAM locations. | The firmware version takes the following form: XXYYT
|  |  | X – Major | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1675 | --- | 1 | INT16U | R | 00 – 99 | 0 | Not supported in PM5xxx. Space reserved to preserve NVRAM locations.
|  |  | Y – Minor | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1676 | --- | 1 | INT16U | R | 0000 – 9999 | 0 | Not supported in PM5xxx. Space reserved to preserve NVRAM locations.
|  |  | Z – Quality | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1677 | --- | 1 | INT16U | R | 0000 – 9999 | 0 | Not supported in PM5xxx. Space reserved to preserve NVRAM locations.
|  |  | T – Internal evolutions | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1678 | --- | 1 | INT16U | R | 0000 – 9999 | 0 | Not supported in PM5xxx. Space reserved to preserve NVRAM locations.
| Firmware Download DLF Interface |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1747 | --- |  | --- | --- | --- | --- | These registers are used by DLF-3000 for firmware downloads.
|  |  | Download – CRC of Last FW Download | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1747 | --- | 1 | INT16U | R | --- | 0
|  |  | Download – Flash Write Failure | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1748 | --- | 1 | INT16U | R | --- | 0
|  |  | Download – % Complete | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1749 | --- | 1 | INT16U | R | 0 – 100 | 0
|  |  | Reserved For Download Software Use | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1750 | --- | 1 | INT16U | RW | --- | 0
|  |  | Download Mode | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1751 | --- |  | --- | --- | --- | ---
| Meter Resets | [11 empty] | 1822 | --- |  | --- | --- | --- | ---
|  |  | Number of Control Power Failures | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1829 | --- | 1 | INT16U | R | --- | 0
|  |  | Cause of Last Meter Reset | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1836 | --- | 1 | INT16U | R | 0 - 2 | 0 | 0 = Unknown 1 = Reset command 2 = Power failure
| Security |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1880 | --- |  | --- | --- | --- | ---
|  | Passwords |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1880 | --- |  | --- | --- | --- | ---
|  |  | Setup Password | Y | Y | Y | Y | Y | Y | Y | Y | Y | 1880 | --- | 4 | UTF8 | WC | --- | "0000"
|  |  | Energy Reset Password | Y | Y |  | Y | Y | Y | Y | Y | Y | 1884 | --- | 4 | UTF8 | WC | --- | "0000"
|  |  | Demand Reset Password | Y | Y |  |  |  | Y | Y |  | Y | 1888 | --- | 4 | UTF8 | WC | --- | "0000"
Meter Setup & Status | [12 empty] | 2000 | --- |  | --- | --- | --- | ---
Miscellaneous Control & Status
|  |  | Meter Operation Timer | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2004 | seconds | 2 | INT32U | R | --- | 0
| Metering Setup |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2014 | --- |  | --- | --- | --- | ---
|  | Power System |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2014 | --- |  | --- | --- | --- | ---
|  |  | Number of Phases | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2014 | --- | 1 | INT16U | RWC | 1 or 3 | 3 | Must match Power System Configuration Enumeration
|  |  | Number of Wires | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2015 | --- | 1 | INT16U | RWC | 2 – 4 | 4 | Must match Power System Configuration Enumeration
|  |  | Power System Configuration | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2016 | --- | 1 | INT16U | RWC | 0 – 12 PM5350: 0 - 12 | 11 | 0 = 1ph, 2w, LN 1 = 1ph, 2w, LL 2 = 1ph, 3w, LL with N 3 = 3ph, 3w, Delta, Ungrounded 4 = 3ph, 3w, Delta, Corner Grounded 5 = 3ph, 3w, Wye, Ungrounded 6 = 3ph, 3w, Wye Grounded 7 = 3ph, 3w, Wye, Resistance Grounded 8 = 3ph, 4w, Open Delta, Center-Tapped 9 = 3ph, 4w, Delta, Center-Tapped 10 = 3ph, 4w, Wye, Ungrounded 11 = 3ph, 4w, Wye Grounded 12 = 3ph, 4w, Wye, Resistance Grounded
|  |  | Nominal Frequency | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2017 | Hz | 1 | INT16U | RWC | 50, 60, 400 PM5350: 50, 60 | 50 | PM5350 does not support 400Hz
|  |  | Nominal Voltage | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2018 | V | 2 | FLOAT32 | RWC | 0 – (2xVT Primary or 2,000,000) | 230 |  | 690 for VT Connection Type == Direct Connect
|  |  | Nominal Current | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2020 | A | 2 | FLOAT32 | RWC | 0 – (4xCT Primary or 50,000) | 5
|  |  | Nominal Power Factor | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2022 | --- | 2 | 4Q_FP_PF | RWC | +/- 0.0 – 2.0 | 0.8
|  |  | Normal Phase Rotation | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2024 | --- | 1 | INT16U | RWC | 0 – 1 | 0
|  | Instrument Transformers 1 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2025 | --- |  | --- | --- | --- | ---
|  |  | Number VTs | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2025 | --- | 1 | INT16U | RWC | Depends on Power System | 0
|  |  | VT Primary | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2026 | V | 2 | FLOAT32 | RWC | VT Secondary – 1,000,000 | 120
|  |  | VT Secondary | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2028 | V | 1 | INT16U | RWC | 100, 110, 115, 120 | 120
|  |  | Number CTs | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2029 | --- | 1 | INT16U | RWC | Depends on Power System | 0
|  |  | CT Primary | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2030 | A | 1 | INT16U | RWC | 1 – 32,767 | 5
|  |  | CT Secondary | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2031 | A | 1 | INT16U | RWC | 1 , 5 | 5
|  |  | CT Primary N | R | R | R | R | R | R | R | R | R | 2032 | A | 1 | INT16U | RWC | 1 – 32,767 | 5
|  |  | CT Secondary N | R | R | R | R | R | R | R | R | R | 2033 | A | 1 | INT16U | RWC | 1, 5 | 5
|  |  | CT Location for 1 or 2 CT Metering | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2034 | --- | 1 | INT16U | RWC | 1 – 3 | 1 | If 1 CT, value is meter terminal connected If 2 CT, value is meter terminal not connected 1 = Phase A, 2 = Phase B, 3 = Phase C
|  |  | VT Location for 1 or 2 VT Metering | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2035 | --- | 1 | INT16U | RWC | 1 – 3 | 1 | Must match CT Location
|  |  | VT Connection Type | Y | Y | Y | Y | Y | Y | Y | Y | Y | 2036 | --- | 1 | INT16U | RWC | 0 –4 | 0 | 0 = Direct Connect 1 = Delta (2 VT) 2 = Wye (3 VT) 3 = L-N (1 VT) 4 = L-L (1 VT) 5 = L-L W/N (2 VT)
| Energy Pulse Output Setup |  |  | Y | Y |  |  | Y | Y | Y | Y | Y | 2126 | --- |  | --- | --- | --- | ---
|  |  | Alarm / Energy LED Mode | Y | Y |  |  | Y | Y | Y | Y | Y | 2126 | --- | 1 | INT16U | RWC | 0 – 2 | 1 | 0 = Disable, 1 = Active Alarm (default), 2 = Energy
|  | Energy Pulse Output Channel 01 |  | Y | Y |  |  | Y | Y | Y | Y | Y | 2130 | ---
|  |  | Energy Channel | Y | Y |  |  | Y | Y | Y | Y | Y | 2130 | --- | 1 | INT16U | RWC | 0 – 18 PM5350 / PM5500: 0 - 9 | 0 | 0 = Not Used 1 = Active Energy Delivered (Into Load) 2 = Active Energy Received (Out of Load) 3 = Active Energy Delivered + Received 4 = Reactive Energy Delivered 5 = Reactive Energy Received 6 = Reactive Energy Delivered + Received 7 = Apparent Energy Delivered 8 = Apparent Energy Received 9 = Apparent Energy Delivered + Received 10 = Active Energy Delivered Phase A 11 = Active Energy Delivered Phase B 12 = Active Energy Delivered Phase C 13 = Reactive Energy Delivered Phase A 14 = Reactive Energy Delivered Phase B 15 = Reactive Energy Delivered Phase C 16 = Apparent Energy Delivered Phase A 17 = Apparent Energy Delivered Phase B 18 = Apparent Energy Delivered Phase C
|  |  | Digital Output Association | Y | Y |  |  | Y | Y | Y | Y | Y | 2131 | --- | 1 | INT16U | RWC | 99 | 0 | 0 = No association 1 - 2 = Digital Output 99 = LED A digital output shall be permitted to be associated with only 1 energy value. If the Energy Channel is not 0, a valid digital output association must be made.
|  |  | Pulse Weight | Y | Y |  |  | Y | Y | Y | Y | Y | 2132 | --- | 2 | FLOAT32/INT32U | RWC | 1E-10 – 1E10 | 0 | If the Energy Channel is not 0, a non-zero pulse weight must be entered. In PM5500 and PM5350 R2 it is an INT32U. The range is 1-9999999, the default value is 1, and the units are pulses / k_h.
Meter Data (Basic) |  |  |  | Y | Y |  |  | Y | Y | Y | Y | Y | 2700 | --- |  | --- | --- | --- | ---
| Energy - 32 bit floating point values |  |  | Y | Y |  |  | Y | Y | Y | Y | Y | 2700 | --- |  | --- | --- | --- | --- |  | Alternate to INT64 format
|  | Accumulated Energy - 32 bit floating point values |  | Y | Y |  |  | Y | Y | Y | Y | Y | 2700 | --- |  | --- | --- | --- | --- |  | Alternate to INT64 format
|  |  | Active Energy Delivered (Into Load) | Y | Y |  |  | Y | Y | Y | Y | Y | 2700 | kWh | 2 | FLOAT32 | R | --- | 0 | Into Load/ Utiltiy Energy | Alternate to INT64 format
|  |  | Active Energy Received (Out of Load) | Y | Y | [5 empty] | Y | Y | 2702 | kWh | 2 | FLOAT32 | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG) | Alternate to INT64 format
|  |  | Active Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 2704 | kWh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Active Energy Delivered- Received | [9 empty] | 2706 | kWh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Reactive Energy Delivered | Y | Y |  |  | Y | Y | Y | Y | Y | 2708 | kVARh | 2 | FLOAT32 | R | --- | 0 | Into Load/ Utiltiy Energy | Alternate to INT64 format
|  |  | Reactive Energy Received | Y | Y | [5 empty] | Y | Y | 2710 | kVARh | 2 | FLOAT32 | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG) | Alternate to INT64 format
|  |  | Reactive Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 2712 | kVARh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Reactive Energy Delivered - Received | [9 empty] | 2714 | kVARh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Apparent Energy Delivered | Y | Y |  |  | Y | Y | Y | Y | Y | 2716 | kVAh | 2 | FLOAT32 | R | --- | 0 | Into Load/ Utiltiy Energy | Alternate to INT64 format
|  |  | Apparent Energy Received | Y | Y | [5 empty] | Y | Y | 2718 | kVAh | 2 | FLOAT32 | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG) | Alternate to INT64 format
|  |  | Apparent Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 2720 | kVAh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Apparent Energy Delivered - Received | [9 empty] | 2722 | kVAh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  | Energy by Quadrant - 32 bit floating point values | [10 empty] | 2724 | --- |  | --- | --- | --- | --- |  | Alternate to INT64 format
|  |  | Reactive Energy in Quadrant I | Y | Y |  |  | Y | Y | Y | Y | Y | 2732 | kVARh | 2 | FLOAT32 | R | --- | 0 | Into Load/ Utiltiy Energy | Alternate to INT64 format
|  |  | Reactive Energy in Quadrant II | Y | Y |  |  | Y | Y | Y | Y | Y | 2734 | kVARh | 2 | FLOAT32 | R | --- | 0 | Into Load/ Utiltiy Energy | Alternate to INT64 format
|  |  | Reactive Energy in Quadrant III | Y | Y | [5 empty] | Y | Y | 2736 | kVARh | 2 | FLOAT32 | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG) | Alternate to INT64 format
|  |  | Reactive Energy in Quadrant IV | Y | Y | [5 empty] | Y | Y | 2738 | kVARh | 2 | FLOAT32 | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG) | Alternate to INT64 format
Meter Data (Basic) |  |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 3000 | --- |  | --- | --- | --- | ---
| 1s Metering (50/60 Cycles) |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 3000 | --- |  | --- | --- | --- | ---
|  | Current |  | Y | Y | Y | Y | Y | Y | Y |  | Y | 3000 | --- |  | --- | --- | --- | ---
|  |  | Current A | Y | Y | Y | Y | Y | Y | Y |  | Y | 3000 | A | 2 | FLOAT32 | R
|  |  | Current B | Y | Y | Y | Y | Y | Y | Y |  | Y | 3002 | A | 2 | FLOAT32 | R
|  |  | Current C | Y | Y | Y | Y | Y | Y | Y |  | Y | 3004 | A | 2 | FLOAT32 | R
|  |  | Current N | Y | Y | Y | Y | Y | Y | Y |  | Y | 3006 | A | 2 | FLOAT32 | R |  |  | Reportable only in systems where there is a N current and when all wired phase currents are metered
|  |  | Current G | Y | Y | Y | Y | Y | Y | Y |  | Y | 3008 | A | 2 | FLOAT32 | R |  |  | Reportable only in systems where there is not a N current and when all wired phase currents are metered
|  |  | Current Avg | Y | Y | Y | Y | Y | Y | Y |  | Y | 3010 | A | 2 | FLOAT32 | R
|  | Current Unbalance |  | Y | Y | Y | Y | Y | Y | Y |  | Y | 3012 | --- |  | --- | --- | --- | ---
|  |  | Current Unbalance A | Y | Y | Y | Y | Y | Y | Y |  | Y | 3012 | % | 2 | FLOAT32 | R
|  |  | Current Unbalance B | Y | Y | Y | Y | Y | Y | Y |  | Y | 3014 | % | 2 | FLOAT32 | R
|  |  | Current Unbalance C | Y | Y | Y | Y | Y | Y | Y |  | Y | 3016 | % | 2 | FLOAT32 | R
|  |  | Current Unbalance Worst | Y | Y | Y | Y | Y | Y | Y |  | Y | 3018 | % | 2 | FLOAT32 | R
|  | Voltage |  | Y | Y | Y | Y | Y | Y | Y |  | Y | 3020 | --- |  | --- | --- | --- | ---
|  |  | Voltage A-B | Y | Y | Y | Y |  | Y | Y |  | Y | 3020 | V | 2 | FLOAT32 | R
|  |  | Voltage B-C | Y | Y | Y | Y |  | Y | Y |  | Y | 3022 | V | 2 | FLOAT32 | R
|  |  | Voltage C-A | Y | Y | Y | Y |  | Y | Y |  | Y | 3024 | V | 2 | FLOAT32 | R
|  |  | Voltage L-L Avg | Y | Y | Y | Y |  | Y | Y |  | Y | 3026 | V | 2 | FLOAT32 | R
|  |  | Voltage A-N | Y | Y | Y | Y |  | Y | Y |  | Y | 3028 | V | 2 | FLOAT32 | R |  |  | Reportable only in systems where Van is connected
|  |  | Voltage B-N | Y | Y | Y | Y |  | Y | Y |  | Y | 3030 | V | 2 | FLOAT32 | R |  |  | Reportable only in systems where Vbn is connected
|  |  | Voltage C-N | Y | Y | Y | Y |  | Y | Y |  | Y | 3032 | V | 2 | FLOAT32 | R |  |  | Reportable only in systems where Vcn is connected
|  |  | Voltage N-G | [9 empty] | 3034 | V | 2 | FLOAT32 | R |  |  | Need to indicate under what conditions this value will be reported.
|  |  | Voltage L-N Avg | Y | Y | Y | Y |  | Y | Y |  | Y | 3036 | V | 2 | FLOAT32 | R |  |  | Reportable only in systems where a L-N voltage is applied
|  | Voltage Unbalance |  | Y | Y | Y | Y |  | Y | Y |  | Y | 3038 | --- |  | --- | --- | --- | ---
|  |  | Voltage Unbalance A-B | Y | Y | Y | Y |  | Y | Y |  | Y | 3038 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance B-C | Y | Y | Y | Y |  | Y | Y |  | Y | 3040 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance C-A | Y | Y | Y | Y |  | Y | Y |  | Y | 3042 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance L-L Worst | Y | Y | Y | Y |  | Y | Y |  | Y | 3044 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance A-N | Y | Y | Y | Y |  | Y | Y |  | Y | 3046 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance B-N | Y | Y | Y | Y |  | Y | Y |  | Y | 3048 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance C-N | Y | Y | Y | Y |  | Y | Y |  | Y | 3050 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance L-N Worst | Y | Y | Y | Y |  | Y | Y |  | Y | 3052 | % | 2 | FLOAT32 | R
|  | Power |  | Y | Y |  |  | Y | Y | Y | Y | Y | 3054 | --- |  | --- | --- | --- | ---
|  |  | Active Power A | Y | Y |  |  | Y | Y | Y | Y | Y | 3054 | kW | 2 | FLOAT32 | R
|  |  | Active Power B | Y | Y |  |  | Y | Y | Y | Y | Y | 3056 | kW | 2 | FLOAT32 | R
|  |  | Active Power C | Y | Y |  |  | Y | Y | Y | Y | Y | 3058 | kW | 2 | FLOAT32 | R
|  |  | Active Power Total | Y | Y |  |  | Y | Y | Y | Y | Y | 3060 | kW | 2 | FLOAT32 | R
|  |  | Reactive Power A | Y | Y |  |  | Y | Y | Y | Y | Y | 3062 | kVAR | 2 | FLOAT32 | R
|  |  | Reactive Power B | Y | Y |  |  | Y | Y | Y | Y | Y | 3064 | kVAR | 2 | FLOAT32 | R
|  |  | Reactive Power C | Y | Y |  |  | Y | Y | Y | Y | Y | 3066 | kVAR | 2 | FLOAT32 | R
|  |  | Reactive Power Total | Y | Y |  |  | Y | Y | Y | Y | Y | 3068 | kVAR | 2 | FLOAT32 | R
|  |  | Apparent Power A | Y | Y |  |  | Y | Y | Y | Y | Y | 3070 | kVA | 2 | FLOAT32 | R
|  |  | Apparent Power B | Y | Y |  |  | Y | Y | Y | Y | Y | 3072 | kVA | 2 | FLOAT32 | R
|  |  | Apparent Power C | Y | Y |  |  | Y | Y | Y | Y | Y | 3074 | kVA | 2 | FLOAT32 | R
|  |  | Apparent Power Total | Y | Y |  |  | Y | Y | Y | Y | Y | 3076 | kVA | 2 | FLOAT32 | R
|  | Power Factor |  | Y | Y | Y | Y |  | Y | Y | Y | Y | 3078 | --- |  | --- | --- | --- | ---
|  |  | Power Factor A | Y | Y | Y | Y |  | Y | Y | Y | Y | 3078 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0
|  |  | Power Factor B | Y | Y | Y | Y |  | Y | Y | Y | Y | 3080 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0
|  |  | Power Factor C | Y | Y | Y | Y |  | Y | Y | Y | Y | 3082 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0
|  |  | Power Factor Total | Y | Y | Y | Y |  | Y | Y | Y | Y | 3084 | --- | 2 | 4Q_FP_PF | R | +/- 0.0 – 2.0
|  | Frequency |  | Y | Y | Y | Y |  | Y | Y |  | Y | 3110 | --- |  | --- | --- | --- | ---
|  |  | Frequency | Y | Y | Y | Y |  | Y | Y |  | Y | 3110 | Hz | 2 | FLOAT32 | R | 42 – 70
|  | Power Factor, Alternate Format | [10 empty] | 3192
|  |  | Power Factor Total IEC | Y | Y | Y | Y |  | Y | Y | Y | Y | 3192 | --- | 2 | FLOAT32 | R | -1 to 1 | ---
|  |  | Power Factor Total Lead Lag | Y | Y | Y | Y |  | Y | Y | Y | Y | 3194 | --- | 2 | FLOAT32 | R | -1 to 1 | ---
|  |  | Power Factor Total IEC | Y | Y | Y | Y |  | Y | Y | Y | Y | 3196 | --- | 1 | INT16U | R | -1 to 1 | --- | If a negative value is reported, add 32768 then divide by 1000 to find the lagging PF reported. If the number is positive just divide that number by 1000 to get the PF reported.
|  |  | Power Factor Total Lead Lag | Y | Y | Y | Y |  | Y | Y | Y | Y | 3197 | --- | 1 | INT16U | R | -1 to 1 | --- | If a negative value is reported, add 32768 then divide by 1000 to find the lagging PF reported. If the number is positive just divide that number by 1000 to get the PF reported.
| Energy |  |  | Y | Y |  |  | Y | Y | Y | Y | Y | 3200 | --- |  | --- | --- | --- | ---
|  | Accumulated Energy |  | Y | Y |  |  | Y | Y | Y | Y | Y | 3200 | --- |  | --- | --- | --- | ---
|  |  | Accumulated Energy Reset Date/Time | [9 empty] | 3200 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Active Energy Delivered (Into Load) | Y | Y |  |  | Y | Y | Y | Y | Y | 3204 | Wh | 4 | INT64 | R | --- | 0 | Into Load/ Utiltiy Energy
|  |  | Active Energy Received (Out of Load) | Y | Y | [5 empty] | Y | Y | 3208 | Wh | 4 | INT64 | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG)
|  |  | Active Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 3212 | Wh | 4 | INT64 | R | --- | 0
|  |  | Active Energy Delivered- Received | [7 empty] | R | R | 3216 | Wh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Delivered | Y | Y |  |  | Y | Y | Y | Y | Y | 3220 | VARh | 4 | INT64 | R | --- | 0 | Into Load/ Utiltiy Energy
|  |  | Reactive Energy Received | Y | Y | [5 empty] | Y | Y | 3224 | VARh | 4 | INT64 | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG)
|  |  | Reactive Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 3228 | VARh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Delivered - Received | [7 empty] | R | R | 3232 | VARh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Delivered | Y | Y |  |  | Y | Y | Y | Y | Y | 3236 | VAh | 4 | INT64 | R | --- | 0 | Into Load/ Utiltiy Energy
|  |  | Apparent Energy Received | Y | Y | [5 empty] | Y | Y | 3240 | VAh | 4 | INT64 | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG)
|  |  | Apparent Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 3244 | VAh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Delivered - Received | [7 empty] | R | R | 3248 | VAh | 4 | INT64 | R | --- | 0
|  | Energy by Quadrant | [10 empty] | 3252 | --- |  | --- | --- | --- | ---
|  |  | Reactive Energy in Quadrant I | Y | Y |  |  | Y | Y | Y | Y | Y | 3272 | VARh | 4 | INT64 | R | --- | 0 | Into Load/ Utiltiy Energy
|  |  | Reactive Energy in Quadrant II | Y | Y |  |  | Y | Y | Y | Y | Y | 3276 | VARh | 4 | INT64 | R | --- | 0 | Into Load/ Utiltiy Energy
|  |  | Reactive Energy in Quadrant III | Y | Y | [5 empty] | Y | Y | 3280 | VARh | 4 | INT64 | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG)
|  |  | Reactive Energy in Quadrant IV | Y | Y | [5 empty] | Y | Y | 3284 | VARh | 4 | INT64 | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG)
| Demand |  |  | Y | Y |  |  |  |  | Y |  | Y | 3701 | --- |  | --- | --- | --- | ---
|  | Demand System 1 (Power) |  | Y | Y |  |  |  |  | Y |  | Y | 3701 | --- |  | --- | --- | --- | --- | Power
|  |  | Power Demand Method | Y | Y |  |  |  |  | Y |  | Y | 3701 | --- | 1 | INT16U | RWC | 0-11 PM5350: 0-7 | 2 | 0 = Thermal Demand 1 = Timed Interval Sliding Block 2 = Timed Interval Block 3 = Timed Interval Rolling Block 4 = Input Synchronized Block 5 = Input Synchronized Rolling Block 6 = Command Synchronized Block 7 = Command Synchronized Rolling Block 8 = Clock Synchronized Block 9 = Clock Synchronized Rolling Block 10 = Slave to System 1 (Power) Demand Interval 11 = Slave to Incremental Energy Interval | PM11xxH supports 1 = Timed Interval Sliding Block 2 = Timed Interval Block 3 = Timed Interval Rolling Block
|  |  | Power Demand Interval Duration | Y | Y |  |  |  |  | Y |  | Y | 3702 | minutes | 1 | INT16U | RWC | 1 – 60 | 15
|  |  | Power Demand Subinterval Duration | Y | Y |  |  |  |  | Y |  | Y | 3703 | minutes | 1 | INT16U | RWC | 1 – 60 | 15 | The value must be evenly divisable into Interval Duration for Rolling Block. For Thermal and Fixed Block demand methods, this value must be same as Interval Duration.
|  | Demand Channel 1 (Active Power) |  | Y | Y |  |  |  |  | Y |  | Y | 3761 | --- |  | --- | --- | --- | --- | Active Power Total
|  |  | Last Demand | Y | Y |  |  |  |  | Y |  | Y | 3764 | kW | 2 | FLOAT32 | R | --- | 0
|  |  | Present Demand | Y | Y |  |  |  |  | Y |  | Y | 3766 | kW | 2 | FLOAT32 | R | --- | 0
|  |  | Predicted Demand | R | R |  |  |  |  | R |  | R | 3768 | kW | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand | Y | Y |  |  |  |  | Y |  | Y | 3770 | kW | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand DateTime | R | R |  |  |  |  | R |  | R | 3772 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Unused | [9 empty] | 3776 | --- | 1 | INT16U | R |  | N/A
|  | Demand Channel 2 (Reactive Power) |  | Y | Y |  |  |  |  | Y |  | Y | 3777 | --- |  | --- | --- | --- | --- | Reactive Power Total
|  |  | Last Demand | Y | Y |  |  |  |  | Y |  | Y | 3780 | kVAR | 2 | FLOAT32 | R | --- | 0
|  |  | Present Demand | Y | Y |  |  |  |  | Y |  | Y | 3782 | kVAR | 2 | FLOAT32 | R | --- | 0
|  |  | Predicted Demand | R | R |  |  |  |  | R |  | R | 3784 | kVAR | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand | Y | Y |  |  |  |  | Y |  | Y | 3786 | kVAR | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand DateTime | R | R |  |  |  |  | R |  | R | 3788 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Unused | [9 empty] | 3792 | --- | 1 | INT16U | R |  | N/A
|  | Demand Channel 3 (Apparent Power) |  | Y | Y |  |  |  |  | Y |  | Y | 3793 | --- |  | --- | --- | --- | --- | Apparent Power Total
|  |  | Last Demand | Y | Y |  |  |  |  | Y |  | Y | 3796 | kVA | 2 | FLOAT32 | R | --- | 0
|  |  | Present Demand | Y | Y |  |  |  |  | Y |  | Y | 3798 | kVA | 2 | FLOAT32 | R | --- | 0
|  |  | Predicted Demand | R | R |  |  |  |  | R |  | R | 3800 | kVA | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand | Y | Y |  |  |  |  | Y |  | Y | 3802 | kVA | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand DateTime | R | R |  |  |  |  | R |  | R | 3804 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Unused | [9 empty] | 3808 | --- | 1 | INT16U | R |  | N/A
|  | Miscellaneous Demand Setup & Data | [10 empty] | 4145 | --- |  | --- | --- | --- | ---
|  |  | Time Remaining for DM | Y | Y |  |  |  |  | Y |  | Y | 4148 | Minutes | 1 | INT16U | R | 1 to 30 | 15
|  |  | Peak demand Activet Power - Gen | [8 empty] | Y | 4149 |  | 2 | FLOAT32 | R | --- | 0 | Applicable for PM1130 model
|  |  | Peak demand Reactive Power- Gen | [8 empty] | Y | 4155 |  | 2 | FLOAT32 | R | --- | 0 | Applicable for PM1130 model
|  |  | Peak demand Apparent Power - Gen | [8 empty] | Y | 4161 |  | 2 | FLOAT32 | R | --- | 0 | Applicable for PM1130 model
Command Interface |  |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5000 | --- |  | --- | --- | --- | ---
| Protected Command Interface |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5000 | --- |  | --- | --- | --- | ---
|  | Command parameters |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5000 | --- |  | --- | --- | --- | ---
|  |  | Requested Command | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5000 | --- | 1 | INT16U | RW | 1 – 32767 | 0
|  |  | Command Semaphore | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5001 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 001 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5002 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 002 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5003 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 003 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5004 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 004 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5005 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 005 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5006 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 006 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5007 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 007 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5008 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 008 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5009 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 009 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5010 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 010 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5011 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 011 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5012 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 012 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5013 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 013 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5014 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 014 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5015 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 015 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5016 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 016 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5017 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 017 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5018 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 018 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5019 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 019 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5020 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 020 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5021 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 021 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5022 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 022 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5023 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 023 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5024 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 024 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5025 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 025 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5026 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 026 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5027 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 027 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5028 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 028 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5029 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 029 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5030 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 030 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5031 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 031 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5032 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 032 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5033 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 033 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5034 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 034 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5035 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 035 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5036 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 036 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5037 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 037 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5038 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 038 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5039 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 039 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5040 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 040 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5041 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 041 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5042 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 042 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5043 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 043 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5044 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 044 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5045 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 045 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5046 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 046 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5047 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 047 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5048 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 048 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5049 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 049 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5050 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 050 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5051 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 051 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5052 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 052 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5053 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 053 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5054 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 054 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5055 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 055 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5056 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 056 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5057 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 057 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5058 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 058 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5059 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 059 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5060 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 060 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5061 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 061 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5062 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 062 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5063 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 063 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5064 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 064 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5065 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 065 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5066 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 066 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5067 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 067 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5068 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 068 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5069 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 069 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5070 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 070 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5071 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 071 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5072 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 072 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5073 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 073 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5074 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 074 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5075 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 075 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5076 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 076 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5077 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 077 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5078 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 078 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5079 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 079 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5080 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 080 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5081 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 081 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5082 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 082 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5083 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 083 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5084 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 084 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5085 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 085 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5086 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 086 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5087 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 087 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5088 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 088 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5089 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 089 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5090 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 090 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5091 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 091 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5092 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 092 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5093 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 093 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5094 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 094 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5095 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 095 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5096 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 096 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5097 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 097 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5098 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 098 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5099 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 099 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5100 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 100 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5101 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 101 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5102 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 102 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5103 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 103 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5104 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 104 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5105 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 105 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5106 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 106 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5107 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 107 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5108 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 108 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5109 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 109 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5110 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 110 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5111 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 111 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5112 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 112 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5113 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 113 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5114 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 114 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5115 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 115 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5116 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 116 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5117 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 117 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5118 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 118 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5119 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 119 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5120 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 120 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5121 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 121 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5122 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 122 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5123 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 123 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5124 | --- | 1 | INT16U | RW | --- | 0
|  | Command result parameters |  | R | R | R | R | R | R | R | R | R | 5125 | ---
|  |  | Command Status | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5125 | --- | 1 | INT16U | R | 0 – 32767 | 0
|  |  | Command Result | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5126 | --- | 1 | INT16U | R | --- | 0 | 0 = Valid Operation 2000 = Command Only Allowed In Calibration Setup 2001 = Command Not Allowed In Calibration Setup 2002 = Command Only Allowed For Disabled Calibration 2003 = Calibration Parameters Not Monotonic 2004 = Calibration Parameters Not Within Percent Range 2005 = Calibration Incomplete Calibration 2006 = Calibration Current Magnitude Phase Shift Mismatch 3000 = Invalid Command 3001 = Invalid Parameter 3002 = Invalid Number of Parameters 3003 = Invalid Password 3004 = Command Failed Security Check 3005 = Invalid Command Interface 3006 = Revenue Security Active 3007 = Operation Not Performed 3008 = Invalid ID 3009 = Feature Not Supported 3010 = Invalid Semaphore 6000 = Invalid Control Mode 6001 = Digital Output Disabled 8000 = File System Error
|  |  | Command Data 001 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5127 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 002 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5128 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 003 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5129 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 004 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5130 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 005 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5131 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 006 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5132 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 007 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5133 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 008 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5134 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 009 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5135 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 010 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5136 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 011 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5137 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 012 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5138 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 013 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5139 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 014 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5140 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 015 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5141 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 016 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5142 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 017 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5143 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 018 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5144 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 019 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5145 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 020 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5146 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 021 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5147 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 022 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5148 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 023 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5149 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 024 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5150 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 025 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5151 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 026 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5152 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 027 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5153 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 028 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5154 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 029 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5155 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 030 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5156 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 031 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5157 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 032 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5158 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 033 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5159 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 034 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5160 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 035 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5161 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 036 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5162 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 037 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5163 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 038 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5164 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 039 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5165 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 040 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5166 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 041 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5167 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 042 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5168 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 043 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5169 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 044 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5170 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 045 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5171 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 046 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5172 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 047 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5173 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 048 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5174 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 049 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5175 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 050 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5176 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 051 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5177 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 052 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5178 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 053 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5179 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 054 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5180 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 055 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5181 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 056 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5182 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 057 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5183 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 058 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5184 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 059 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5185 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 060 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5186 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 061 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5187 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 062 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5188 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 063 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5189 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 064 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5190 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 065 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5191 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 066 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5192 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 067 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5193 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 068 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5194 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 069 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5195 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 070 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5196 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 071 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5197 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 072 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5198 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 073 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5199 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 074 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5200 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 075 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5201 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 076 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5202 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 077 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5203 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 078 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5204 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 079 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5205 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 080 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5206 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 081 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5207 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 082 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5208 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 083 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5209 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 084 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5210 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 085 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5211 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 086 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5212 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 087 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5213 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 088 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5214 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 089 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5215 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 090 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5216 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 091 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5217 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 092 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5218 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 093 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5219 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 094 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5220 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 095 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5221 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 096 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5222 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 097 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5223 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 098 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5224 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 099 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5225 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 100 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5226 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 101 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5227 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 102 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5228 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 103 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5229 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 104 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5230 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 105 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5231 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 106 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5232 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 107 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5233 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 108 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5234 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 109 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5235 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 110 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5236 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 111 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5237 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 112 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5238 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 113 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5239 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 114 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5240 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 115 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5241 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 116 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5242 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 117 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5243 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 118 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5244 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 119 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5245 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 120 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5246 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 121 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5247 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 122 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5248 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 123 | Y | Y | Y | Y | Y | Y | Y | Y | Y | 5249 | --- | 1 | INT16U | R | --- | 0
|  | Favourite(Config) Page data |  | Y | Y |  |  |  | Y | Y |  | Y
|  |  | Parameter1 address | Y | Y |  |  |  | Y | Y |  | Y | 6100 | --- | 1 | INT16U | RWC | --- | 3010 | Current Avg = 3010 Voltage L-L Avg = 3026 Voltage L-N Avg = 3036 Active Power Total = 3060 Reactive Power Total = 3068 Apparent Power Total = 3076 Power Factor Total = 3084 Frequency = 3110
|  |  | Parameter2 address | Y | Y |  |  |  | Y | Y |  | Y | 6101 | --- | 1 | INT16U | RWC | --- | 3084 | Current Avg = 3010 Voltage L-L Avg = 3026 Voltage L-N Avg = 3036 Active Power Total = 3060 Reactive Power Total = 3068 Apparent Power Total = 3076 Power Factor Total = 3084 Frequency = 3110
|  |  | Parameter3 address | Y | Y |  |  |  | Y | Y |  | Y | 6102 | --- | 1 | INT16U | RWC | --- | 3036 | Current Avg = 3010 Voltage L-L Avg = 3026 Voltage L-N Avg = 3036 Active Power Total = 3060 Reactive Power Total = 3068 Apparent Power Total = 3076 Power Factor Total = 3084 Frequency = 3110
|  |  | Parameter4 address | R | R |  |  |  | R | R |  | R | 6103 | --- | 1 | INT16U | RWC | --- | 0xFFFF
Communications |  |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 6500 | --- |  | --- | --- | --- | ---
| RS-485 Base |  |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 6500 | --- |  | --- | --- | --- | ---
|  | RS-485 Base Port 1 Settings |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 6500 | --- |  | --- | --- | --- | ---
|  |  | RS-485 Comm Port (M/S) Protocol | Y | Y | Y | Y | Y | Y | Y | Y | Y | 6500 | --- | 1 | INT16U | RWC | 0 – 3 | 0 | 0 = Modbus 1 = Jbus 2 = Modbus ASCII 8-Bit 3 = Modbus ASCII 7-Bit
|  |  | RS-485 Comm Port (M/S) Address | Y | Y | Y | Y | Y | Y | Y | Y | Y | 6501 | --- | 1 | INT16U | RWC | 1 – 255 | 1 | Valid Addresses: Modbus: 1 – 247 Jbus: 1 – 255
|  |  | RS-485 Comm Port (M/S) Baud Rate | Y | Y | Y | Y | Y | Y | Y | Y | Y | 6502 | --- | 1 | INT16U | RWC | 0 – 2 | 1 | 0 = 9600 1 = 19200 2 = 38400 For PM2000,EM6400, EM72xx, Hybrid 0 = 4800 1 = 9600 2 = 19200 3 = 38400
|  |  | RS-485 Comm Port (M/S) Parity | Y | Y | Y | Y | Y | Y | Y | Y | Y | 6503 | --- | 1 | INT16U | RWC | 0 – 2 | 0 | 0 = Even 1 = Odd 2 = None
Inputs & Outputs | [12 empty] | 7000 | --- |  | --- | --- | --- | ---
| Hybrid | [10 empty] | Y | 9600
|  | Digital Output status | [9 empty] | Y | 9600
|  |  | DO1(Relay1) Status | [8 empty] | Y | 9600 | --- | 1 | INT16U | R | 0 - 1 | 0 | 0 = OFF, 1=ON
|  |  | Type | [8 empty] | Y | 9601 | --- | 1 | INT16U | R | 0 - 2 | 0 | 0 = None, 1=Over, 2=Under
|  |  | Source | [8 empty] | Y | 9602 |  | 1 | INT16U | R | 0 - 2 | 0 | 0 = None, 1=EB, 2=DG
|  |  | Parameter caused by Relay1 ON | [8 empty] | Y | 9603 | --- | 1 | INT16U | R | MB address of Parameter | 0 | MB address of Parameter
|  | Digital Output Setup | [9 empty] | Y | 9610
|  | Relay 1 | [9 empty] | Y | 9610 | ---
|  |  | Parameter1 associated to DO1 | [8 empty] | Y | 9610 |  | 1 | INT16U | R | MS address of parameter | --- | MS address of parameter Current Avg = 3010 Voltage L-L Avg = 3026 Voltage L-N Avg = 3036 Active Power Total = 3060 Reactive Power Total = 3068 Apparent Power Total = 3076 Power Factor Total = 3084 Frequency = 3110 Present demand: Active Power = 3766, Reactive Power = 3782, Apparent power: 3798 Command mode = 9600 Prepaid Energy = 9638
|  |  | Source | [8 empty] | Y | 9611 | --- | 1 | INT16U | R | 1 - 2 | 2 | 1=Utility, 2=Generator, 3=Both
|  |  | Upper Limit | [8 empty] | Y | 9612 | --- | 2 | FLOAT32 | R | --- | --- | --- | The Upper Limit value allowed is the maximum CT/PT ratio of present configuration of CT ratio.
|  |  | Lower Limit | [8 empty] | Y | 9614 | --- | 2 | FLOAT32 | R | --- | --- | --- | must be < Upper Limit
|  |  | Time Delay | [8 empty] | Y | 9616 | Sec | 1 | INT16U | R | 1 to 60 | 5 | Sec | For Prepaid option, delay must be 1 sec
|  |  | Parameter2 Associated to DO1 | [8 empty] | Y | 9617 | --- | 1 | INT16U | R | MS address of parameter | --- | MS address of parameter Current Avg = 3010 Voltage L-L Avg = 3026 Voltage L-N Avg = 3036 Active Power Total = 3060 Reactive Power Total = 3068 Apparent Power Total = 3076 Power Factor Total = 3084 Frequency = 3110 Present demand: Active Power = 3766, Reactive Power = 3782, Apparent power: 3798
|  |  | Source | [8 empty] | Y | 9618 | --- | 1 | INT16U | R | 1 - 2 | 2 | 1=Utility, 2=Generator, 3=Both
|  |  | Upper Limit | [8 empty] | Y | 9619 | --- | 2 | FLOAT32 | R | --- | --- | --- | The Upper Limit value allowed is the maximum CT/PT ratio of present configuration of CT ratio.
|  |  | Lower Limit | [8 empty] | Y | 9621 | --- | 2 | FLOAT32 | R | --- | --- | --- | must be < Uppler Limit
|  |  | Time Delay | [8 empty] | Y | 9623 | Sec | 1 | INT16U | R | 1 to 60 | 5 | Sec
Prepaid Energy
|  |  | Prepaid Energy Balance | [8 empty] | Y | 9638 | k_h | 2 | FLOAT32 | R | --- | ---
Meter Data (Advanced) | [12 empty] | 21000 | --- |  | --- | --- | --- | ---
| Power Quality (1 to 3 Seconds) |  |  | Y | Y |  |  |  |  | Y |  | Y | 21300 | --- |  | --- | --- | --- | ---
|  | Total Harmonic Distortion, Current |  | Y | Y |  |  |  |  | Y |  | Y | 21300 | --- |  | --- | --- | --- | ---
|  |  | THD Current A | Y | Y |  |  |  |  | Y |  | Y | 21300 | % | 2 | FLOAT32 | R | 0 – 100 | --- | THD = (RMS of harmonics / RMS of fundamental) * 100
|  |  | THD Current B | Y | Y |  |  |  |  | Y |  | Y | 21302 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Current C | Y | Y |  |  |  |  | Y |  | Y | 21304 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  | Total Harmonic Distortion, Voltage |  | Y | Y |  |  |  |  | Y |  | Y | 21322 | --- |  | --- | --- | --- | ---
|  |  | THD Voltage A-B | Y | Y |  |  |  |  | Y |  | Y | 21322 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage B-C | Y | Y |  |  |  |  | Y |  | Y | 21324 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage C-A | Y | Y |  |  |  |  | Y |  | Y | 21326 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage A-N | Y | Y |  |  |  |  | Y |  | Y | 21330 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage B-N | Y | Y |  |  |  |  | Y |  | Y | 21332 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage C-N | Y | Y |  |  |  |  | Y |  | Y | 21334 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  | Hybrid EXT Basic Setup |  | Y | Y | Y | Y | Y | Y | Y | Y | Y | 42283 | --- |  | --- | --- | ---
|  |  | A.Suppression | Y | Y | Y | Y | Y | Y | Y | Y | Y | 42283 | mA | 1 | INT16U | RWC | 5 to 99 | 5
|  |  | FS% | Y | Y | Y | Y | Y | Y | Y | Y | Y | 42284 | --- | 1 | INT16U | RWC | 1 to 100 | 100
|  |  | Parameter selection (Power) | Y | Y | R | R | Y | Y | Y | Y | Y | 42285 | --- | 1 | INT16U | RWC | 1- VA, 2-W, 3-VAR | 2
|  |  | Demand Parameter selection | Y | Y | R | R | R | R | Y | R | Y | 42286 | --- | 1 | INT16U | RWC | 1- VA, 2-W, 3-VAR | 1
|  |  | Poles | Y | Y | Y | Y | R | R | Y | Y | Y | 42287 | --- | 1 | INT16U | RWC | 2 to 16 step of 2 | 4
|  |  | Label | Y | Y | Y | Y | Y | Y | Y | Y | Y | 42288 | --- | 1 | INT16U | RWC | 1- 123, 2-Abc, 3-rst, 4-pqr, 5-ryb | 123
|  |  | Source1 name | R | R | R | R | R | R | R | Y | Y | 42289 | --- | 1 | INT16U | RWC | 0 to 33 | 30
|  |  | Source2 name | R | R | R | R | R | R | R | Y | Y | 42290 | --- | 1 | INT16U | RWC | 0 to 33 | 16
|  | OLD register (Last cleared Energy Registers) - 32 bit floating point values |  | Y | Y |  |  | Y | Y | Y | Y | Y | 42976 | --- |  | --- | --- |  |  |  | Alternate to INT64 format
|  |  | Active Energy Delivered (Into Load) | Y | Y |  |  | Y | Y | Y | Y | Y | 42976 | kWh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Active Energy Received (Out of Load) | Y | Y | [5 empty] | Y | Y | 42978 | kWh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Active Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 42980 | kWh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Active Energy Delivered – Received | [7 empty] | R | R | 42982 | kWh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Reactive Energy Delivered | Y | Y |  |  | Y | Y | Y | Y | Y | 42984 | kVARh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Reactive Energy Received | Y | Y | [5 empty] | Y | Y | 42986 | kVARh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Reactive Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 42988 | kVARh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Reactive Energy Delivered – Received | [7 empty] | R | R | 42990 | kVARh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Apparent Energy Delivered | Y | Y |  |  | Y | Y | Y | Y | Y | 42992 | kVAh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Apparent Energy Received | Y | Y | [5 empty] | Y | Y | 42994 | kVAh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Apparent Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 42996 | kVAh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
|  |  | Apparent Energy Delivered – Received | [7 empty] | R | R | 42998 | kVAh | 2 | FLOAT32 | R | --- | 0 |  | Alternate to INT64 format
| Percent of load (current) |  |  | Y | Y | Y | Y | Y | Y | Y |  | Y | 43500 | --- |  | --- | --- | --- | ---
|  |  | Current A load % | Y | Y | Y | Y | Y | Y | Y |  | Y | 43500 | % | 2 | FLOAT32 | R | --- | 0
|  |  | Current B load % | Y | Y | Y | Y | Y | Y | Y |  | Y | 43502 | % | 2 | FLOAT32 | R | --- | 0
|  |  | Current C load % | Y | Y | Y | Y | Y | Y | Y |  | Y | 43504 | % | 2 | FLOAT32 | R | --- | 0
|  |  | Current avg load % | Y | Y | Y | Y | Y | Y | Y |  | Y | 43506 | % | 2 | FLOAT32 | R | --- | 0
| Current phase angles | [11 empty] | 43508 | --- |  | --- | ---
|  |  | Phase angle between Voltage A and Current A | Y | Y | Y | Y |  | Y | Y |  | Y | 43508 | --- | 2 | FLOAT32 | R | --- | 0
|  |  | Phase angle between Voltage B and Current B | Y | Y | Y | Y |  | Y | Y |  | Y | 43510 | --- | 2 | FLOAT32 | R | --- | 0
|  |  | Phase angle between Voltage C and Current C | Y | Y | Y | Y |  | Y | Y |  | Y | 43512 | --- | 2 | FLOAT32 | R | --- | 0
| RPM |  |  | Y | Y | Y | Y |  |  | Y | Y | Y | 43520 | --- |  | --- | --- | --- | ---
|  |  | RPM | Y | Y | Y | Y |  |  | Y | Y | Y | 43520 | --- | 2 | FLOAT32 | R | --- | 0
| Timer counters |  |  | Y | Y |  |  | Y | Y | Y | Y | Y | 43546 | --- |  | --- | --- | --- | ---
|  |  | Run sec Delivered (Into Load) | Y | Y |  |  | Y | Y | Y | Y | Y | 43546 | seconds | 2 | INT32U | R | --- | 0
|  |  | Run sec Received (Out of Load) | Y | Y | [5 empty] | Y | Y | 43548 | seconds | 2 | INT32U | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG)
|  |  | Run sec Total | Y | Y | [5 empty] | Y | Y | 43558 | --- | 2 | INT32U | R | --- | 0
| OLD register (Last cleared Energy Registers) |  |  | Y | Y |  |  | Y | Y | Y | Y | Y | 43600 | --- |  | --- | ---
|  |  | Active Energy Delivered (Into Load) | Y | Y |  |  | Y | Y | Y | Y | Y | 43600 | Wh | 4 | INT64U | R | --- | 0
|  |  | Active Energy Received (Out of Load) | Y | Y | [5 empty] | Y | Y | 43604 | Wh | 4 | INT64U | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG)
|  |  | Active Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 43608 | Wh | 4 | INT64U | R | --- | 0
|  |  | Active Energy Delivered – Received | [7 empty] | R | R | 43612 | Wh | 4 | INT64U | R | --- | 0
|  |  | Reactive Energy Delivered | Y | Y |  |  | Y | Y | Y | Y | Y | 43616 | VARh | 4 | INT64U | R | --- | 0
|  |  | Reactive Energy Received | Y | Y | [5 empty] | Y | Y | 43620 | VARh | 4 | INT64U | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG)
|  |  | Reactive Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 43624 | VARh | 4 | INT64U | R | --- | 0
|  |  | Reactive Energy Delivered – Received | [7 empty] | R | R | 43628 | VARh | 4 | INT64U | R | --- | 0
|  |  | Apparent Energy Delivered | Y | Y |  |  | Y | Y | Y | Y | Y | 43632 | VAh | 4 | INT64U | R | --- | 0
|  |  | Apparent Energy Received | Y | Y | [5 empty] | Y | Y | 43636 | VAh | 4 | INT64U | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG)
|  |  | Apparent Energy Delivered + Received | Y | Y | [5 empty] | Y | Y | 43640 | VAh | 4 | INT64U | R | --- | 0
|  |  | Apparent Energy Delivered – Received | [7 empty] | R | R | 43644 | VAh | 4 | INT64U | R | --- | 0
|  |  | Run sec Delivered (Into Load) | Y | Y |  |  | Y | Y | Y | Y | Y | 43672 | seconds | 2 | INT32U | R | --- | 0
|  |  | Run sec Received (Out of Load) | Y | Y | [5 empty] | Y | Y | 43674 | seconds | 2 | INT32U | R | --- | 0 | For EM6438H, PM1130H, This reguster is mapped to Alternate source (Gen/DG)
|  |  | Run sec total | Y | Y | [5 empty] | Y | Y | 43684 | --- | 2 | INT32U | R | --- | 0
Note on T1: Native Range of Data Type unless noted otherwise.

## Commands
Subsystem | Command Name | Command Number | Command Tag | EM6459H | DM6200H | EM76433H | Em6436H | PM1120H | Em6438H | PM1130H | Publish | Parameters |  | User Notes
REGISTER_ACCESS (0-999) |  |  |  | Y | Y | Y | Y | Y | Y | Y | Y
| Reset Subsystem(s) to Default | 1 | C_RESET_SUBSYS_TO_DEFAULT | Y | Y | Y | Y | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Subsystems) (3) Subsystem ID or -1 (For All Subsystems) |  | Subsystem IDs 0 = Register Access 1 = System 2 = Metering 3 = Commands 4 = HMI 5 = Communications 6 = IO 7 = Alarms 8 = Files 9 = Diagnostics 10 = Security
SYSTEM (1000-1999) |  |  |  | Y | Y | Y | Y | Y | Y | Y | Y
| Warm Start Reset | 1000 | C_WARM_START_RESET | Y | Y | Y | Y | Y | Y | Y | Y | (1) Command Semaphore |  | This command does not provide a command status or result.
| Reset Power Fail Counter | 1002 | C_RESET_POWER_FAIL_COUNT | Y | Y | Y | Y | Y | Y | Y | Y | (1) Command Semaphore
| Meter Name Setup | 1008 | C_METER_NAME_SETUP | Y | Y | Y | Y | Y | Y | Y | Y | (1) Command Semaphore (2-21 ) Meter Name
METERING (2000-2999) |  |  |  | Y | Y | Y | Y | Y | Y | Y | Y
| Basic Meter Setup | 2000 | C_BASIC_METER_SETUP | Y | Y | Y | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Number of Phases (3) Number of Wires (4) Power System Configuration (5) Nominal Frequency (6-7) Nominal Voltage (8-9) Nominal Current (10-11) Nominal Power Factor (12) Normal Phase Rotation | (13) Number VTs (14-15) VT Primary (16) VT Secondary (17) Number CTs (18) CT Primary, Phase (19) CT Secondary, Phase (20) CT Primary, Neutral (21) CT Secondary, Neutral (22) CT Location for 1 CT Metering (23) VT Location for 1 VT Metering (24) VT Connection Type
| Demand System Setup | 2002 | C_DMD_SETUP |  |  |  |  | Y |  | Y | Y | (1) Command Semaphore (2) Demand System ID (3) Demand Method (4) Demand Interval Duration (5) Demand Subinterval Duration |  | Demand System ID 1 = Power 2 = Current 3 = Input Metering
| Energy Pulse Output Setup | 2003 | C_ENERGY_PULSE_OUTPUT_SETUP |  |  | Y | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Energy Channel (3) Digital Output ID (4-5) Pulse Weight (6) Energy Channel (7) Digital Output ID (8-9) Pulse Weight (10) Energy Channel (11) Digital Output ID (12-13) Pulse Weight |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 99 = Energy LED
| Preset Accumuated Energy | 2006 | C_PRESET_ACCUMULATED_ENG |  |  | Y | Y | Y | Y | Y | Y | (1) Command Semaphore (2-5) Active Energy Delivered (Into Load) (6-9) Active Energy Received (Out of Load) (10-13) Reactive Energy Delivered (14-17) Reactive Energy Received (18-21) Apparent Energy Delivered (22-25) Apparent Energy Received
| Reset All Peak Demands | 2015 | C_RESET_ALL_PEAK_DMDS |  |  |  |  | Y |  | Y | Y | (1) Command Semaphore
| Reset All Accumulated Energies | 2021 | C_RESET_ALL_ACC_ENG |  |  | Y | Y | Y | Y | Y | Y | (1) Command Semaphore
| Meter Initialization | 2037 | C_METER_INITIALIZATION | Y | Y | Y | Y | Y | Y | Y | Y | (1) Command Semaphore |  | Resets Energy, Demand, Demand peaks, Min/Max, Alarm counters, Alarm logs, Alarm event queue, IO Counters, IO Timers, Active Load Timer, Comm diagnostics, power fail counter, cycle counter Data logs (Scout only), and Waveform capture Files (Scout only).
| Energy / Alarm LED Enable | 2039 | C_ENERGY_LED_ENABLE |  |  | Y | Y | Y | Y | Y | Y | (1) Command Semaphore (2) 0 = Disable / 1 = Alarm / 2 = Energy, In Hybrid models, Alarm not applicable
| Basic Extended Setup Hybrid | 2959 | C_EXT_BASICSETUP_HYBRID | Y | Y | Y | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Current Suppression (3) Full scale Percentage (4) Parameter selection (5) Demand Parameter selection (6) Poles (7) Label (8) Dual Source name1 (9) Dual Source name2
HMI (4000-4999) | [10 empty] | Y
| HMI_CONFIG_PAGE_LED | 4008 | C_HMI_CONFIG_PAGE |  |  |  | Y | Y |  | Y | Y | (1) Command Semaphore (2) Register Address of parameter (ROW1) (3) Register Address of Parameter (ROW2) (4) Register Address of Parameter (ROW3) (5) Register Address of Parameter (ROW4) |  | EM64xxH_PM11xxH Supports 3 parameters. 4th Parameter is reserved
COMMUNICATIONS (5000-5999) |  |  |  | Y | Y | Y | Y | Y | Y | Y | Y
| Communications Setup | 5000 | C_COMMS_SETUP | Y | Y | Y | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Communications Port ID (3) RS-485 Comm Port (M/S) Protocol (4) RS-485 Comm Port (M/S) Address (5) RS-485 Comm Port (M/S) Baud Rate (6) RS-485 Comm Port (M/S) Parity (7) RS-485 Comm Port (M/S) Modbus ASCII Default Timeout |  | Communications Port ID 1 = Standard RS-485
IO (6000-6999) | [10 empty] | Y
| De-energize Digital Output | 6002 | C_DE_ENERGIZE_DO | [6 empty] | Y | Y | (1) Command Semaphore (2) Digital Output ID
| Energize Digital Output | 6003 | C_ENERGIZE_DO | [6 empty] | Y | Y | (1) Command Semaphore (2) Digital Output ID
| Relay (Digital Output)Setup(Hybrid) | 6504 | C_DO_SETUP_HYBRID | [6 empty] | Y | Y | (1) Command Semaphore (2) Relay No (3) Parameter1 associated to DO1 (4) Source selection (5-6) Upper Limit (7-8) Lower Limit (9) Time Delay (10) Parameter2 associated to DO1 (11) Source selection (12-13) Upper Limit (14-15) Lower Limit (16) Time Delay | Relay no: 1 = Relay1, 2-Relay2 Parameter1 = Reg Address of Parameter associtaed to relay1 Source selection = 0 = None, 1 = Utility, 2=Gen 3= Util+Gen Upper Limit & Lower Limit = Parameter value Time delay = 1 to 60 Sec

## Data Types
Data Type | Description | Native Range | N/A Value | Notes
UTF8 | Alphanumeric | 0-3 bytes | 0x00
INT16 | Signed Integer, 16 bits | -32,768 - 32,767 | 0x8000
INT16U | Unsigned Integer, 16 bits | 0 - 65,535 | 0xFFFF
INT32 | Signed Integer, 32 bits | -2,147,483,648 – 2,147,483,647 | 0x80000000
INT32U | Unsigned Integer, 32 bits | 0 - 4,294,967,295 | 0xFFFFFFFF
INT64 | Signed Integer, 64 bits |  | 0x8000000000000000
FLOAT32 | Floating Point, 32 bits | +/- 1*10^38 | 0xFFC00000
FLOAT64 | Floating Point, 64 bits | +/-1.798*10^308 | 0xFFF8000000000000
BITMAP |  |  | 0x8000 Example for a status bitmap 1 register long. | For status bitmaps that are multiple registers long, the most significant bit will be set to indicate the entire bitmap is N/A.This does not apply to configuration bitmaps. So, in setup commands that include a bitmap as a parameter, the user must always include the desired value for these bitmaps.
DATETIME | DateTime | 1/1/2000 – 12/31/2127 | 0xFFFFFFFFFFFFFFFF | DateTime coding format using 4 words as per IEC 870-5-4 Word 1 b0-b6: Year (0 - 127) b7-b15: Reserved Word 2 b0-b4: Day (1-31) b5-b7: Weekday (1-7, 0 if not used) b8-b11: Month (1-12) b12-b15: Reserved Word 3 b0-b5: Minutes (0-59) b6: Reserved b7: Time synchronization quality, 1 = non valid or non synchronization b8-b12: Hour (0-23) b13-b14: Reserved b15: 0 = Standard time, 1 = Daylight Savings Time Word 4 b0-b15: Millisecond (0 - 59999)
DATE | Date |  | 0xFFFFFFFF | Word 1 b0-b7: Year (0 - 99) b8-b15: Reserved Word 2 b0-b4: Day (1-31) b5-b7: Weekday (1-7, 0 if not used) b8-b11: Month (1-12) b12-b15: Reserved
TIME | Time |  | 0xFFFFFFFF | Word 1 b0-b5: Minutes (0-59) b6: Reserved b7: Time synchronization quality, 1 = non valid or non synchronization b8-b12: Hour (0-23) b13-b14: Reserved b15: 0 = Standard time, 1 = Daylight Savings Time Word 2 b0-b15: Millisecond (0 - 59999)
PORTAL | A portal provides a means to access data of a size up to 125 registers by doing a Modbus block read of a single register. This allows large data sets to be accessed without using a large number of registers. An example might be a data type of PORTAL100 located at register 1000. In order to read the 100 registers, the user would do a block read of 100 registers beginning at register 1000. The data at PORTAL100 could be stored in an internal format and presented to the user by the meter communications firmware as 100 16 bit quantities.
4Q FP PF | Four Quadrant Floating Point Power Factor | -2 - 2 | 0xFFC00000 | Power factor values are specially encoded floating point values. Angle of complex power = power factor register value 0° = 1 90° = 0 180° = -1 270° = 2 Q1: 0 < x < 1 Q2: -2 < x < -1 Q3: -1 < x < 0 Q4: 1 < x < 2 Pseudo code to decode PF Value if (rigVal > 1) { PF_Val = 2 - regVal; PF is leading } else if (regVal < -1) { PF_Val = -2-regVal PF is leading } else if ( abs(regVal) equals 1 ) { PF_Val = regVal PF is at unity } else { PF_Val = regVal PF is lagging }

## Units Codes
Code | Abbreviation | Description
0 |  | No Units
1 | % | Percentage
2 | °C | Degrees Celsius
3 | °F | Degrees Fahrenheit
4 | Deg | Degrees Angular
5 | Hz | Hertz
6 | A | amperes
7 | kA | Kilo Amperes
8 | V | Volts
9 | kV | Kilo Volts
10 | MV | Mega Volts
11 | W | Watts
12 | kW | Kilowatts
13 | MW | Megawatts
14 | VAR | Volt-Ampere Reactive
15 | kVAR | Kilo Volt-Ampere Reactive
16 | MVAR | Mega Volt-Ampere Reactive
17 | VA | Volt-Amperes
18 | kVA | Kilo Volt-Amperes
19 | MVA | Mega Volt-Amperes
20 | WH | Watt-Hour
21 | kWH | Kilowatt-Hour
22 | MWH | Megawatt-Hour
23 | VARH | Reactive Volt-Ampere Hour
24 | kVARH | Reactive Kilo Volt-Ampere Hour
25 | MVARH | Reactive Mega Volt-Ampere Hour
26 | VAH | Volt-Ampere Hours
27 | kVAH | Kilo Volt-Ampere Hours
28 | MVAH | Mega Volt-Ampere Hours
29 | Seconds | Seconds
30 | Minutes | Minutes
31 | Hours | Hours
32 | Bytes (RAM) | Bytes
33 | kBytes (RAM) | Kilobytes
34 | $ | Dollars
35 | gal | gallons
36 | gal/hr | gallons/hour
37 | gal/min | gallons/minute
38 | cfm | cubic feet/min
39 | PSI | PSI
40 | BTU | BTU
41 | L | liters
42 | ton-hours | ton-hours
43 | l/hr | liters/hour
44 | l/min | liters/min
45 | € | Euros
46 | ms | Milliseconds
47 | m³ | cubic-meters
48 | m³/sec | cubic-meters/sec
49 | m³/min | cubic-meters/min
50 | m³/hr | cubic-meters/hour
51 | Pa | pascals
52 | Bars | bar
53 | RPM | Revolutions/min
55 | BTU/hr | BTU/hour
56 | PSIG | Pounds/square inch gauge
57 | SCFM | Standard cubic feet/min
58 | MCF | Thousand cubic feet
59 | Therm | Therm
60 | SCFH | Standard cubic feet/hour
61 | PSIA | pounds/square inch absolute
62 | lbs | pounds
63 | kg | Kilogram
64 | klbs | Kilopounds
65 | lb/hr | pound/hour
66 | ton/hr | ton/hour
67 | kg/hr | Kilogram/hour
68 | in. Hg | inch of Mercury
69 | kPa | kiloPascals
70 | %RH | percentage of relative humidity
71 | MPH | miles per hour
72 | m/sec | meters/sec
73 | mV/cal/(cm²/min) | milliVolts/calorie/(square centimeters/min)
74 | in | inches
75 | mm | millimeter
76 | GWH | GigaWatt-Hour
77 | GVARH | Reactive Giga Volt-Ampere Hour
78 | GVAH | Giga Volt-Ampere Hours
79 | AH | Ampere-Hours
80 | kAH | Kiloamp-Hours
81 | Therm/hr | Therm/hour

## Publish
APPENDIX C - REGISTER LIST
|  |  | Reg | Name | Size | Type | Access | NV | Units | Notes
System Setup & Status
Product & Features
|  |  | 30 | Meter Name | 20 | UTF8 | RWC | Y | ---
|  |  | 50 | Meter Model | 20 | UTF8 | RWC | Y | ---
|  |  | 70 | Manufacturer | 20 | UTF8 | RWC | Y | ---
|  |  | 90 | Product ID Number | 1 | INT16U | RWC | Y | --- | PM5350 = 15234
Manufacturing Data
Meter
|  |  | 130 | Serial Number | 2 | INT32U | R | Y | ---
|  |  | 132 | Date of Manufacture | 4 | DATETIME | R | Y | ---
|  |  | 136 | Hardware Revision | 5 | UTF8 | R | Y | ---
Firmware Versions
Operating System
|  |  | 1637 | Present Firmware Version (DLF Format) X.Y.T | 1 | INT16U | R | Y | --- | The firmware version takes the following form: XXYYT
|  |  | 1638 | X – Major | 1 | INT16U | R | Y | ---
|  |  | 1639 | Y – Minor | 1 | INT16U | R | Y | ---
|  |  | 1640 | Z – Quality | 1 | INT16U | R | Y | ---
|  |  | 1642 | Previous Firmware Version (DLF Format) X.Y.T | 1 | INT16U | R | Y | --- | The firmware version takes the following form: XXYYT
|  |  | 1643 | X – Major | 1 | INT16U | R | Y | ---
|  |  | 1644 | Y – Minor | 1 | INT16U | R | Y | ---
|  |  | 1645 | Z – Quality | 1 | INT16U | R | Y | ---
|  |  | 1647 | Date/Time of Last Firmware Download | 4 | DATETIME | R | Y | ---
Reset
|  |  | 1669 | Present Firmware Version (DLF Format) X.Y.T | 1 | INT16U | R | Y | --- | The firmware version takes the following form: XXYYT
Language
|  |  | 1701 | Present Firmware Version (DLF Format) X.Y.T | 1 | INT16U | R | Y | --- | The firmware version takes the following form: XXYYT
Meter Resets
|  |  | 1824 | Last Unit Restart DateTime | 4 | DATETIME | R | Y | ---
|  |  | 1828 | Number of Metering System Restarts | 1 | INT16U | R | Y | ---
|  |  | 1829 | Number of Control Power Failures | 1 | INT16U | R | Y | ---
|  |  | 1830 | Date/Time of Last Control Power Failure | 4 | DATETIME | R | Y | ---
|  |  | 1834 | Duration of Last Control Power Failure | 2 | INT32U | R | Y | seconds
|  |  | 1836 | Cause of Last Meter Reset | 1 | INT16U | R | Y | --- | 0 = Unknown 1 = Reset command 2 = Power failure
Timekeeping
Present Date & Time (7 register format)
|  |  | 1837 | Year | 1 | INT16U | R | N | year
|  |  | 1838 | Month | 1 | INT16U | R | N | month
|  |  | 1839 | Day | 1 | INT16U | R | N | days
|  |  | 1840 | Hour | 1 | INT16U | R | N | hours
|  |  | 1841 | Minute | 1 | INT16U | R | N | minutes
|  |  | 1842 | Second | 1 | INT16U | R | N | seconds
|  |  | 1843 | Millisecond | 1 | INT16U | R | N | msec
Present Date & Time (4 register format)
|  |  | 1845 | Year | 1 | INT16U | R | N | ---
|  |  | 1846 | Month & Day | 1 | INT16U | R | N | ---
|  |  | 1847 | Hour & Minute | 1 | INT16U | R | N | ---
|  |  | 1848 | Milliseconds | 1 | INT16U | R | N | ---
Security
Revenue Security
|  |  | 1920 | Revenue Security Switch Status | 1 | INT16U | R | Y | --- | 0 = disabled, 1 = enabled
|  |  | 1921 | Revenue Security Status | 1 | INT16U | R | Y | --- | 0 = inactive, 1 = active
|  |  | 1922 | Date/Time of Last Revenue Security State Change | 4 | DATETIME | R | Y | ---
Meter Setup & Status
Miscellaneous Control & Status
|  |  | 2002 | Active Load Timer | 2 | INT32U | R | Y | seconds | Increments when average current exceeds the Active Load Timer Setpoint.
|  |  | 2004 | Meter Operation Timer | 2 | INT32U | R | Y | seconds
Metering Setup
Power System
|  |  | 2014 | Number of Phases | 1 | INT16U | RWC | Y | --- | Must match Power System Configuration Enumeration
|  |  | 2015 | Number of Wires | 1 | INT16U | RWC | Y | --- | Must match Power System Configuration Enumeration
|  |  | 2016 | Power System Configuration | 1 | INT16U | RWC | Y | --- | 0 = 1ph, 2w, LN 1 = 1ph, 2w, LL 2 = 1ph, 3w, LL with N 3 = 3ph, 3w, Delta, Ungrounded 4 = 3ph, 3w, Delta, Corner Grounded 5 = 3ph, 3w, Wye, Ungrounded 6 = 3ph, 3w, Wye Grounded 7 = 3ph, 3w, Wye, Resistance Grounded 8 = 3ph, 4w, Open Delta, Center-Tapped 9 = 3ph, 4w, Delta, Center-Tapped 10 = 3ph, 4w, Wye, Ungrounded 11 = 3ph, 4w, Wye Grounded 12 = 3ph, 4w, Wye, Resistance Grounded 13 = Multi-Circuit 3 circuit LN 14 = Multi-Circuit 2 Circuit LN ( Not used ) 15 = Multi-Circuit 1 Cicuit LN ( Not used ) 16 = Multi-Circuit 3 Circuit LL ( Not used ) 17 = Multi-Circuit 2 Circuit LL 18 = Multi-Circuit 1 Circuit LL ( Not used ) 19 = Multi-Circuit 1 Circuit LL 1 Circuit LN ( Not used ) 20 = Multi-Circuit Wye
|  |  | 2017 | Nominal Frequency | 1 | INT16U | RWC | Y | Hz | PM5350 does not support 400Hz
|  |  | 2018 | Nominal Voltage | 2 | FLOAT32 | RWC | Y | V
|  |  | 2020 | Nominal Current | 2 | FLOAT32 | RWC | Y | A
|  |  | 2022 | Nominal Power Factor | 2 |  | RWC | Y | ---
|  |  | 2024 | Normal Phase Rotation | 1 | INT16U | RWC | Y | ---
Instrument Transformers
|  |  | 2025 | Number VTs | 1 | INT16U | RWC | Y | ---
|  |  | 2026 | VT Primary | 2 | FLOAT32 | RWC | Y | V
|  |  | 2028 | VT Secondary | 1 | INT16U | RWC | Y | V
|  |  | 2029 | Number CTs | 1 | INT16U | RWC | Y | ---
|  |  | 2030 | CT Primary | 1 | INT16U | RWC | Y | A
|  |  | 2031 | CT Secondary | 1 | INT16U | RWC | Y | A
|  |  | 2034 | CT Location for 1 or 2 CT Metering | 1 | INT16U | RWC | Y | --- | If 1 CT, value is meter terminal connected If 2 CT, value is meter terminal not connected 1 = Phase A, 2 = Phase B, 3 = Phase C
|  |  | 2035 | VT Location for 1 or 2 VT Metering | 1 | INT16U | RWC | Y | --- | Must match CT Location
|  |  | 2036 | VT Connection Type | 1 | INT16U | RWC | Y | --- | 0 = Direct Connect 1 = Delta (2 VT) 2 = Wye (3 VT) 3 = L-N (1 VT) 4 = L-L (1 VT) 5 = L-L W/N (2 VT)
Operating Modes
|  |  | 2048 | Peak Current Demand Over Last Year | 2 | FLOAT32 | RWC | Y | A | Entered by the user for use in calculation of Total Demand Distortion. 0 = Calculation performed using peak demand of 3-phase average current.
|  |  | 2050 | Active Load Timer Setpoint | 2 | FLOAT32 | RWC | Y | A
Energy Pulse Output Setup
Alarm / Energy LED Mode
|  |  | 2126 | Alarm / Energy LED Mode | 1 | INT16U | RWC | Y | --- | 0 = Disable, 1 = Active Alarm (default), 2 = Energy
Energy Pulse Output Channel 01
|  |  | 2130 | Energy Channel | 1 | INT16U | RWC | Y | --- | 0 = Not Used 1 = Active Energy Delivered (Into Load) 2 = Active Energy Received (Out of Load) 3 = Active Energy Delivered + Received 4 = Reactive Energy Delivered 5 = Reactive Energy Received 6 = Reactive Energy Delivered + Received 7 = Apparent Energy Delivered 8 = Apparent Energy Received 9 = Apparent Energy Delivered + Received 10 = Active Energy Delivered Phase A 11 = Active Energy Delivered Phase B 12 = Active Energy Delivered Phase C 13 = Reactive Energy Delivered Phase A 14 = Reactive Energy Delivered Phase B 15 = Reactive Energy Delivered Phase C 16 = Apparent Energy Delivered Phase A 17 = Apparent Energy Delivered Phase B 18 = Apparent Energy Delivered Phase C
|  |  | 2131 | Digital Output Association | 1 | INT16U | RWC | Y | --- | 0 = No association 1 - 2 = Digital Output 99 = LED A digital output shall be permitted to be associated with only 1 energy value. If the Energy Channel is not 0, a valid digital output association must be made.
|  |  | 2132 | Pulse Weight | 2 | FLOAT32 | RWC | Y | kWh, kVAh, kVAh | If the Energy Channel is not 0, a non-zero pulse weight must be entered.
Meter Data (Basic)
1s Metering (50/60 Cycles)
Current
|  |  | 3000 | Current A | 2 | FLOAT32 | R | N | A
|  |  | 3002 | Current B | 2 | FLOAT32 | R | N | A
|  |  | 3004 | Current C | 2 | FLOAT32 | R | N | A
|  |  | 3006 | Current N | 2 | FLOAT32 | R | N | A | Reportable only in systems where there is a N current and when all wired phase currents are metered
|  |  | 3008 | Current G | 2 | FLOAT32 | R | N | A | Reportable only in systems where there is not a N current and when all wired phase currents are metered
|  |  | 3010 | Current Avg | 2 | FLOAT32 | R | N | A
Current Unbalance
|  |  | 3012 | Current Unbalance A | 2 | FLOAT32 | R | N | %
|  |  | 3014 | Current Unbalance B | 2 | FLOAT32 | R | N | %
|  |  | 3016 | Current Unbalance C | 2 | FLOAT32 | R | N | %
|  |  | 3018 | Current Unbalance Worst | 2 | FLOAT32 | R | N | %
Voltage
|  |  | 3020 | Voltage A-B | 2 | FLOAT32 | R | N | V
|  |  | 3022 | Voltage B-C | 2 | FLOAT32 | R | N | V
|  |  | 3024 | Voltage C-A | 2 | FLOAT32 | R | N | V
|  |  | 3026 | Voltage L-L Avg | 2 | FLOAT32 | R | N | V
|  |  | 3028 | Voltage A-N | 2 | FLOAT32 | R | N | V | Reportable only in systems where Van is connected
|  |  | 3030 | Voltage B-N | 2 | FLOAT32 | R | N | V | Reportable only in systems where Vbn is connected
|  |  | 3032 | Voltage C-N | 2 | FLOAT32 | R | N | V | Reportable only in systems where Vcn is connected
|  |  | 3036 | Voltage L-N Avg | 2 | FLOAT32 | R | N | V | Reportable only in systems where a L-N voltage is applied
Voltage Unbalance
|  |  | 3038 | Voltage Unbalance A-B | 2 | FLOAT32 | R | N | %
|  |  | 3040 | Voltage Unbalance B-C | 2 | FLOAT32 | R | N | %
|  |  | 3042 | Voltage Unbalance C-A | 2 | FLOAT32 | R | N | %
|  |  | 3044 | Voltage Unbalance L-L Worst | 2 | FLOAT32 | R | N | %
|  |  | 3046 | Voltage Unbalance A-N | 2 | FLOAT32 | R | N | %
|  |  | 3048 | Voltage Unbalance B-N | 2 | FLOAT32 | R | N | %
|  |  | 3050 | Voltage Unbalance C-N | 2 | FLOAT32 | R | N | %
|  |  | 3052 | Voltage Unbalance L-N Worst | 2 | FLOAT32 | R | N | %
Power
|  |  | 3054 | Active Power A | 2 | FLOAT32 | R | N | kW
|  |  | 3056 | Active Power B | 2 | FLOAT32 | R | N | kW
|  |  | 3058 | Active Power C | 2 | FLOAT32 | R | N | kW
|  |  | 3060 | Active Power Total | 2 | FLOAT32 | R | N | kW
|  |  | 3062 | Reactive Power A | 2 | FLOAT32 | R | N | kVAR
|  |  | 3064 | Reactive Power B | 2 | FLOAT32 | R | N | kVAR
|  |  | 3066 | Reactive Power C | 2 | FLOAT32 | R | N | kVAR
|  |  | 3068 | Reactive Power Total | 2 | FLOAT32 | R | N | kVAR
|  |  | 3070 | Apparent Power A | 2 | FLOAT32 | R | N | kVA
|  |  | 3072 | Apparent Power B | 2 | FLOAT32 | R | N | kVA
|  |  | 3074 | Apparent Power C | 2 | FLOAT32 | R | N | kVA
|  |  | 3076 | Apparent Power Total | 2 | FLOAT32 | R | N | kVA
Power Factor
|  |  | 3078 | Power Factor A | 2 | 4Q FP PF | R | N | ---
|  |  | 3080 | Power Factor B | 2 | 4Q FP PF | R | N | ---
|  |  | 3082 | Power Factor C | 2 | 4Q FP PF | R | N | ---
|  |  | 3084 | Power Factor Total | 2 | 4Q FP PF | R | N | ---
|  |  | 3086 | Displacement Power Factor A | 2 | 4Q FP PF | R | N | ---
|  |  | 3088 | Displacement Power Factor B | 2 | 4Q FP PF | R | N | ---
|  |  | 3090 | Displacement Power Factor C | 2 | 4Q FP PF | R | N | ---
|  |  | 3092 | Displacement Power Factor Total | 2 | 4Q FP PF | R | N | ---
Frequency
|  |  | 3110 | Frequency | 2 | FLOAT32 | R | N | Hz
Miscellaneous
|  |  | 3134 | Phase Rotation | 1 | INT16U | R | N | --- | 0 = ABC, 1 = CBA
Energy
Accumulated Energy
|  |  | 3200 | Accumulated Energy Reset Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 3204 | Active Energy Delivered (Into Load) | 4 | INT64 | R | Y | Wh
|  |  | 3208 | Active Energy Received (Out of Load) | 4 | INT64 | R | Y | Wh
|  |  | 3212 | Active Energy Delivered + Received | 4 | INT64 | R | Y | Wh
|  |  | 3216 | Active Energy Delivered – Received | 4 | INT64 | R | Y | Wh
|  |  | 3220 | Reactive Energy Delivered | 4 | INT64 | R | Y | VARh
|  |  | 3224 | Reactive Energy Received | 4 | INT64 | R | Y | VARh
|  |  | 3228 | Reactive Energy Delivered + Received | 4 | INT64 | R | Y | VARh
|  |  | 3232 | Reactive Energy Delivered – Received | 4 | INT64 | R | Y | VARh
|  |  | 3236 | Apparent Energy Delivered | 4 | INT64 | R | Y | VAh
|  |  | 3240 | Apparent Energy Received | 4 | INT64 | R | Y | VAh
|  |  | 3244 | Apparent Energy Delivered + Received | 4 | INT64 | R | Y | VAh
|  |  | 3248 | Apparent Energy Delivered – Received | 4 | INT64 | R | Y | VAh
Demand
Demand System 1 (Power)
|  |  | 3701 | Power Demand Method | 1 | INT16U | RWC | Y | --- | 0 = Thermal Demand 1 = Timed Interval Sliding Block 2 = Timed Interval Block 3 = Timed Interval Rolling Block 4 = Input Synchronized Block 5 = Input Synchronized Rolling Block 6 = Command Synchronized Block 7 = Command Synchronized Rolling Block 8 = Clock Synchronized Block 9 = Clock Synchronized Rolling Block 10 = Slave to System 1 (Power) Demand Interval 11 = Slave to Incremental Energy Interval
|  |  | 3702 | Power Demand Interval Duration | 1 | INT16U | RWC | Y | minutes
|  |  | 3703 | Power Demand Subinterval Duration | 1 | INT16U | RWC | Y | minutes | The value must be evenly divisable into Interval Duration for Rolling Block. For Thermal and Fixed Block demand methods, this value must be same as Interval Duration.
|  |  | 3704 | Power Demand Elapsed Time in Interval | 1 | INT16U | R | N | seconds
|  |  | 3705 | Power Demand Elapsed Time in Subinterval | 1 | INT16U | R | N | seconds
|  |  | 3706 | Power Demand Peak Reset Date/Time | 4 | DATETIME | R | Y | ---
Demand System 2 (Current)
|  |  | 3711 | Current Demand Method | 1 | INT16U | RWC | Y | --- | 0 = Thermal Demand 1 = Timed Interval Sliding Block 2 = Timed Interval Block 3 = Timed Interval Rolling Block 4 = Input Synchronized Block 5 = Input Synchronized Rolling Block 6 = Command Synchronized Block 7 = Command Synchronized Rolling Block 8 = Clock Synchronized Block 9 = Clock Synchronized Rolling Block 10 = Slave to System 1 (Power) Demand Interval 11 = Slave to Incremental Energy Interval
|  |  | 3712 | Current Demand Interval Duration | 1 | INT16U | RWC | Y | minutes
|  |  | 3713 | Current Demand Subinterval Duration | 1 | INT16U | RWC | Y | minutes | The value must be evenly divisable into Interval Duration for Rolling Block. For Thermal and Fixed Block demand methods, this value must be same as Interval Duration.
|  |  | 3714 | Current Demand Elapsed Time in Interval | 1 | INT16U | R | N | seconds
|  |  | 3715 | Current Demand Elapsed Time in Subinterval | 1 | INT16U | R | N | seconds
|  |  | 3716 | Current Demand Peak Reset Date/Time | 4 | DATETIME | R | Y | ---
Demand Channel 1 (Active Power)
|  |  | 3761 | Demand System Assignment | 1 | INT16U | R | Y | --- | Power Demand
|  |  | 3762 | Register Number of Metered Quantity | 1 | INT16U | R | Y | --- | Active Power Total
|  |  | 3763 | Units Code | 1 | INT16U | R | Y | ---
|  |  | 3764 | Last Demand | 2 | FLOAT32 | R | Y | kW
|  |  | 3766 | Present Demand | 2 | FLOAT32 | R | N | kW
|  |  | 3768 | Predicted Demand | 2 | FLOAT32 | R | N | kW
|  |  | 3770 | Peak Demand | 2 | FLOAT32 | R | Y | kW
|  |  | 3772 | Peak Demand DateTime | 4 | DATETIME | R | Y | ---
Demand Channel 2 (Reactive Power)
|  |  | 3777 | Demand System Assignment | 1 | INT16U | R | Y | --- | Power Demand
|  |  | 3778 | Register Number of Metered Quantity | 1 | INT16U | R | Y | --- | Reactive Power Total
|  |  | 3779 | Units Code | 1 | INT16U | R | Y | ---
|  |  | 3780 | Last Demand | 2 | FLOAT32 | R | Y | kVAR
|  |  | 3782 | Present Demand | 2 | FLOAT32 | R | N | kVAR
|  |  | 3784 | Predicted Demand | 2 | FLOAT32 | R | N | kVAR
|  |  | 3786 | Peak Demand | 2 | FLOAT32 | R | Y | kVAR
|  |  | 3788 | Peak Demand DateTime | 4 | DATETIME | R | Y | ---
Demand Channel 3 (Apparent Power)
|  |  | 3793 | Demand System Assignment | 1 | INT16U | R | Y | --- | Power Demand
|  |  | 3794 | Register Number of Metered Quantity | 1 | INT16U | R | Y | --- | Apparent Power Total
|  |  | 3795 | Units Code | 1 | INT16U | R | Y | ---
|  |  | 3796 | Last Demand | 2 | FLOAT32 | R | Y | kVA
|  |  | 3798 | Present Demand | 2 | FLOAT32 | R | N | kVA
|  |  | 3800 | Predicted Demand | 2 | FLOAT32 | R | N | kVA
|  |  | 3802 | Peak Demand | 2 | FLOAT32 | R | Y | kVA
|  |  | 3804 | Peak Demand DateTime | 4 | DATETIME | R | Y | ---
Demand Channel 8 (Current Avg)
|  |  | 3873 | Demand System Assignment | 1 | INT16U | R | Y | --- | Current Demand
|  |  | 3874 | Register Number of Metered Quantity | 1 | INT16U | R | Y | --- | Current, Average
|  |  | 3875 | Units Code | 1 | INT16U | R | Y | ---
|  |  | 3876 | Last Demand | 2 | FLOAT32 | R | Y | A
|  |  | 3878 | Present Demand | 2 | FLOAT32 | R | N | A
|  |  | 3880 | Predicted Demand | 2 | FLOAT32 | R | N | A
|  |  | 3882 | Peak Demand | 2 | FLOAT32 | R | Y | A
|  |  | 3884 | Peak Demand DateTime | 4 | DATETIME | R | Y | ---
Command Interface
Protected Command Interface
Command parameters
|  |  | 5000 | Requested Command | 1 | INT16U | RW | N | ---
|  |  | 5001 | Command Semaphore | 1 | INT16U | RW | N | ---
|  |  | 5002 | Command Parameter 001 | 1 | INT16U | RW | N | ---
|  |  | 5003 | Command Parameter 002 | 1 | INT16U | RW | N | ---
|  |  | 5004 | Command Parameter 003 | 1 | INT16U | RW | N | ---
|  |  | 5005 | Command Parameter 004 | 1 | INT16U | RW | N | ---
|  |  | 5006 | Command Parameter 005 | 1 | INT16U | RW | N | ---
|  |  | 5007 | Command Parameter 006 | 1 | INT16U | RW | N | ---
|  |  | 5008 | Command Parameter 007 | 1 | INT16U | RW | N | ---
|  |  | 5009 | Command Parameter 008 | 1 | INT16U | RW | N | ---
|  |  | 5010 | Command Parameter 009 | 1 | INT16U | RW | N | ---
|  |  | 5011 | Command Parameter 010 | 1 | INT16U | RW | N | ---
|  |  | 5012 | Command Parameter 011 | 1 | INT16U | RW | N | ---
|  |  | 5013 | Command Parameter 012 | 1 | INT16U | RW | N | ---
|  |  | 5014 | Command Parameter 013 | 1 | INT16U | RW | N | ---
|  |  | 5015 | Command Parameter 014 | 1 | INT16U | RW | N | ---
|  |  | 5016 | Command Parameter 015 | 1 | INT16U | RW | N | ---
|  |  | 5017 | Command Parameter 016 | 1 | INT16U | RW | N | ---
|  |  | 5018 | Command Parameter 017 | 1 | INT16U | RW | N | ---
|  |  | 5019 | Command Parameter 018 | 1 | INT16U | RW | N | ---
|  |  | 5020 | Command Parameter 019 | 1 | INT16U | RW | N | ---
|  |  | 5021 | Command Parameter 020 | 1 | INT16U | RW | N | ---
|  |  | 5022 | Command Parameter 021 | 1 | INT16U | RW | N | ---
|  |  | 5023 | Command Parameter 022 | 1 | INT16U | RW | N | ---
|  |  | 5024 | Command Parameter 023 | 1 | INT16U | RW | N | ---
|  |  | 5025 | Command Parameter 024 | 1 | INT16U | RW | N | ---
|  |  | 5026 | Command Parameter 025 | 1 | INT16U | RW | N | ---
|  |  | 5027 | Command Parameter 026 | 1 | INT16U | RW | N | ---
|  |  | 5028 | Command Parameter 027 | 1 | INT16U | RW | N | ---
|  |  | 5029 | Command Parameter 028 | 1 | INT16U | RW | N | ---
|  |  | 5030 | Command Parameter 029 | 1 | INT16U | RW | N | ---
|  |  | 5031 | Command Parameter 030 | 1 | INT16U | RW | N | ---
|  |  | 5032 | Command Parameter 031 | 1 | INT16U | RW | N | ---
|  |  | 5033 | Command Parameter 032 | 1 | INT16U | RW | N | ---
|  |  | 5034 | Command Parameter 033 | 1 | INT16U | RW | N | ---
|  |  | 5035 | Command Parameter 034 | 1 | INT16U | RW | N | ---
|  |  | 5036 | Command Parameter 035 | 1 | INT16U | RW | N | ---
|  |  | 5037 | Command Parameter 036 | 1 | INT16U | RW | N | ---
|  |  | 5038 | Command Parameter 037 | 1 | INT16U | RW | N | ---
|  |  | 5039 | Command Parameter 038 | 1 | INT16U | RW | N | ---
|  |  | 5040 | Command Parameter 039 | 1 | INT16U | RW | N | ---
|  |  | 5041 | Command Parameter 040 | 1 | INT16U | RW | N | ---
|  |  | 5042 | Command Parameter 041 | 1 | INT16U | RW | N | ---
|  |  | 5043 | Command Parameter 042 | 1 | INT16U | RW | N | ---
|  |  | 5044 | Command Parameter 043 | 1 | INT16U | RW | N | ---
|  |  | 5045 | Command Parameter 044 | 1 | INT16U | RW | N | ---
|  |  | 5046 | Command Parameter 045 | 1 | INT16U | RW | N | ---
|  |  | 5047 | Command Parameter 046 | 1 | INT16U | RW | N | ---
|  |  | 5048 | Command Parameter 047 | 1 | INT16U | RW | N | ---
|  |  | 5049 | Command Parameter 048 | 1 | INT16U | RW | N | ---
|  |  | 5050 | Command Parameter 049 | 1 | INT16U | RW | N | ---
|  |  | 5051 | Command Parameter 050 | 1 | INT16U | RW | N | ---
|  |  | 5052 | Command Parameter 051 | 1 | INT16U | RW | N | ---
|  |  | 5053 | Command Parameter 052 | 1 | INT16U | RW | N | ---
|  |  | 5054 | Command Parameter 053 | 1 | INT16U | RW | N | ---
|  |  | 5055 | Command Parameter 054 | 1 | INT16U | RW | N | ---
|  |  | 5056 | Command Parameter 055 | 1 | INT16U | RW | N | ---
|  |  | 5057 | Command Parameter 056 | 1 | INT16U | RW | N | ---
|  |  | 5058 | Command Parameter 057 | 1 | INT16U | RW | N | ---
|  |  | 5059 | Command Parameter 058 | 1 | INT16U | RW | N | ---
|  |  | 5060 | Command Parameter 059 | 1 | INT16U | RW | N | ---
|  |  | 5061 | Command Parameter 060 | 1 | INT16U | RW | N | ---
|  |  | 5062 | Command Parameter 061 | 1 | INT16U | RW | N | ---
|  |  | 5063 | Command Parameter 062 | 1 | INT16U | RW | N | ---
|  |  | 5064 | Command Parameter 063 | 1 | INT16U | RW | N | ---
|  |  | 5065 | Command Parameter 064 | 1 | INT16U | RW | N | ---
|  |  | 5066 | Command Parameter 065 | 1 | INT16U | RW | N | ---
|  |  | 5067 | Command Parameter 066 | 1 | INT16U | RW | N | ---
|  |  | 5068 | Command Parameter 067 | 1 | INT16U | RW | N | ---
|  |  | 5069 | Command Parameter 068 | 1 | INT16U | RW | N | ---
|  |  | 5070 | Command Parameter 069 | 1 | INT16U | RW | N | ---
|  |  | 5071 | Command Parameter 070 | 1 | INT16U | RW | N | ---
|  |  | 5072 | Command Parameter 071 | 1 | INT16U | RW | N | ---
|  |  | 5073 | Command Parameter 072 | 1 | INT16U | RW | N | ---
|  |  | 5074 | Command Parameter 073 | 1 | INT16U | RW | N | ---
|  |  | 5075 | Command Parameter 074 | 1 | INT16U | RW | N | ---
|  |  | 5076 | Command Parameter 075 | 1 | INT16U | RW | N | ---
|  |  | 5077 | Command Parameter 076 | 1 | INT16U | RW | N | ---
|  |  | 5078 | Command Parameter 077 | 1 | INT16U | RW | N | ---
|  |  | 5079 | Command Parameter 078 | 1 | INT16U | RW | N | ---
|  |  | 5080 | Command Parameter 079 | 1 | INT16U | RW | N | ---
|  |  | 5081 | Command Parameter 080 | 1 | INT16U | RW | N | ---
|  |  | 5082 | Command Parameter 081 | 1 | INT16U | RW | N | ---
|  |  | 5083 | Command Parameter 082 | 1 | INT16U | RW | N | ---
|  |  | 5084 | Command Parameter 083 | 1 | INT16U | RW | N | ---
|  |  | 5085 | Command Parameter 084 | 1 | INT16U | RW | N | ---
|  |  | 5086 | Command Parameter 085 | 1 | INT16U | RW | N | ---
|  |  | 5087 | Command Parameter 086 | 1 | INT16U | RW | N | ---
|  |  | 5088 | Command Parameter 087 | 1 | INT16U | RW | N | ---
|  |  | 5089 | Command Parameter 088 | 1 | INT16U | RW | N | ---
|  |  | 5090 | Command Parameter 089 | 1 | INT16U | RW | N | ---
|  |  | 5091 | Command Parameter 090 | 1 | INT16U | RW | N | ---
|  |  | 5092 | Command Parameter 091 | 1 | INT16U | RW | N | ---
|  |  | 5093 | Command Parameter 092 | 1 | INT16U | RW | N | ---
|  |  | 5094 | Command Parameter 093 | 1 | INT16U | RW | N | ---
|  |  | 5095 | Command Parameter 094 | 1 | INT16U | RW | N | ---
|  |  | 5096 | Command Parameter 095 | 1 | INT16U | RW | N | ---
|  |  | 5097 | Command Parameter 096 | 1 | INT16U | RW | N | ---
|  |  | 5098 | Command Parameter 097 | 1 | INT16U | RW | N | ---
|  |  | 5099 | Command Parameter 098 | 1 | INT16U | RW | N | ---
|  |  | 5100 | Command Parameter 099 | 1 | INT16U | RW | N | ---
|  |  | 5101 | Command Parameter 100 | 1 | INT16U | RW | N | ---
|  |  | 5102 | Command Parameter 101 | 1 | INT16U | RW | N | ---
|  |  | 5103 | Command Parameter 102 | 1 | INT16U | RW | N | ---
|  |  | 5104 | Command Parameter 103 | 1 | INT16U | RW | N | ---
|  |  | 5105 | Command Parameter 104 | 1 | INT16U | RW | N | ---
|  |  | 5106 | Command Parameter 105 | 1 | INT16U | RW | N | ---
|  |  | 5107 | Command Parameter 106 | 1 | INT16U | RW | N | ---
|  |  | 5108 | Command Parameter 107 | 1 | INT16U | RW | N | ---
|  |  | 5109 | Command Parameter 108 | 1 | INT16U | RW | N | ---
|  |  | 5110 | Command Parameter 109 | 1 | INT16U | RW | N | ---
|  |  | 5111 | Command Parameter 110 | 1 | INT16U | RW | N | ---
|  |  | 5112 | Command Parameter 111 | 1 | INT16U | RW | N | ---
|  |  | 5113 | Command Parameter 112 | 1 | INT16U | RW | N | ---
|  |  | 5114 | Command Parameter 113 | 1 | INT16U | RW | N | ---
|  |  | 5115 | Command Parameter 114 | 1 | INT16U | RW | N | ---
|  |  | 5116 | Command Parameter 115 | 1 | INT16U | RW | N | ---
|  |  | 5117 | Command Parameter 116 | 1 | INT16U | RW | N | ---
|  |  | 5118 | Command Parameter 117 | 1 | INT16U | RW | N | ---
|  |  | 5119 | Command Parameter 118 | 1 | INT16U | RW | N | ---
|  |  | 5120 | Command Parameter 119 | 1 | INT16U | RW | N | ---
|  |  | 5121 | Command Parameter 120 | 1 | INT16U | RW | N | ---
|  |  | 5122 | Command Parameter 121 | 1 | INT16U | RW | N | ---
|  |  | 5123 | Command Parameter 122 | 1 | INT16U | RW | N | ---
|  |  | 5124 | Command Parameter 123 | 1 | INT16U | RW | N | ---
|  |  | 5125 | Command Status | 1 | INT16U | R | N | ---
|  |  | 5126 | Command Result | 1 | INT16U | R | N | --- | 0 = Valid Operation 2000 = Command Only Allowed In Calibration Setup 2001 = Command Not Allowed In Calibration Setup 2002 = Command Only Allowed For Disabled Calibration 2003 = Calibration Parameters Not Monotonic 2004 = Calibration Parameters Not Within Percent Range 2005 = Calibration Incomplete Calibration 2006 = Calibration Current Magnitude Phase Shift Mismatch 3000 = Invalid Command 3001 = Invalid Parameter 3002 = Invalid Number of Parameters 3003 = Invalid Password 3004 = Command Failed Security Check 3005 = Invalid Command Interface 3006 = Revenue Security Active 3007 = Operation Not Performed 3008 = Invalid ID 3009 = Feature Not Supported 3010 = Invalid Semaphore 6000 = Invalid Control Mode 6001 = Digital Output Disabled 8000 = File System Error
|  |  | 5127 | Command Data 001 | 1 | INT16U | R | N | ---
|  |  | 5128 | Command Data 002 | 1 | INT16U | R | N | ---
|  |  | 5129 | Command Data 003 | 1 | INT16U | R | N | ---
|  |  | 5130 | Command Data 004 | 1 | INT16U | R | N | ---
|  |  | 5131 | Command Data 005 | 1 | INT16U | R | N | ---
|  |  | 5132 | Command Data 006 | 1 | INT16U | R | N | ---
|  |  | 5133 | Command Data 007 | 1 | INT16U | R | N | ---
|  |  | 5134 | Command Data 008 | 1 | INT16U | R | N | ---
|  |  | 5135 | Command Data 009 | 1 | INT16U | R | N | ---
|  |  | 5136 | Command Data 010 | 1 | INT16U | R | N | ---
|  |  | 5137 | Command Data 011 | 1 | INT16U | R | N | ---
|  |  | 5138 | Command Data 012 | 1 | INT16U | R | N | ---
|  |  | 5139 | Command Data 013 | 1 | INT16U | R | N | ---
|  |  | 5140 | Command Data 014 | 1 | INT16U | R | N | ---
|  |  | 5141 | Command Data 015 | 1 | INT16U | R | N | ---
|  |  | 5142 | Command Data 016 | 1 | INT16U | R | N | ---
|  |  | 5143 | Command Data 017 | 1 | INT16U | R | N | ---
|  |  | 5144 | Command Data 018 | 1 | INT16U | R | N | ---
|  |  | 5145 | Command Data 019 | 1 | INT16U | R | N | ---
|  |  | 5146 | Command Data 020 | 1 | INT16U | R | N | ---
|  |  | 5147 | Command Data 021 | 1 | INT16U | R | N | ---
|  |  | 5148 | Command Data 022 | 1 | INT16U | R | N | ---
|  |  | 5149 | Command Data 023 | 1 | INT16U | R | N | ---
|  |  | 5150 | Command Data 024 | 1 | INT16U | R | N | ---
|  |  | 5151 | Command Data 025 | 1 | INT16U | R | N | ---
|  |  | 5152 | Command Data 026 | 1 | INT16U | R | N | ---
|  |  | 5153 | Command Data 027 | 1 | INT16U | R | N | ---
|  |  | 5154 | Command Data 028 | 1 | INT16U | R | N | ---
|  |  | 5155 | Command Data 029 | 1 | INT16U | R | N | ---
|  |  | 5156 | Command Data 030 | 1 | INT16U | R | N | ---
|  |  | 5157 | Command Data 031 | 1 | INT16U | R | N | ---
|  |  | 5158 | Command Data 032 | 1 | INT16U | R | N | ---
|  |  | 5159 | Command Data 033 | 1 | INT16U | R | N | ---
|  |  | 5160 | Command Data 034 | 1 | INT16U | R | N | ---
|  |  | 5161 | Command Data 035 | 1 | INT16U | R | N | ---
|  |  | 5162 | Command Data 036 | 1 | INT16U | R | N | ---
|  |  | 5163 | Command Data 037 | 1 | INT16U | R | N | ---
|  |  | 5164 | Command Data 038 | 1 | INT16U | R | N | ---
|  |  | 5165 | Command Data 039 | 1 | INT16U | R | N | ---
|  |  | 5166 | Command Data 040 | 1 | INT16U | R | N | ---
|  |  | 5167 | Command Data 041 | 1 | INT16U | R | N | ---
|  |  | 5168 | Command Data 042 | 1 | INT16U | R | N | ---
|  |  | 5169 | Command Data 043 | 1 | INT16U | R | N | ---
|  |  | 5170 | Command Data 044 | 1 | INT16U | R | N | ---
|  |  | 5171 | Command Data 045 | 1 | INT16U | R | N | ---
|  |  | 5172 | Command Data 046 | 1 | INT16U | R | N | ---
|  |  | 5173 | Command Data 047 | 1 | INT16U | R | N | ---
|  |  | 5174 | Command Data 048 | 1 | INT16U | R | N | ---
|  |  | 5175 | Command Data 049 | 1 | INT16U | R | N | ---
|  |  | 5176 | Command Data 050 | 1 | INT16U | R | N | ---
|  |  | 5177 | Command Data 051 | 1 | INT16U | R | N | ---
|  |  | 5178 | Command Data 052 | 1 | INT16U | R | N | ---
|  |  | 5179 | Command Data 053 | 1 | INT16U | R | N | ---
|  |  | 5180 | Command Data 054 | 1 | INT16U | R | N | ---
|  |  | 5181 | Command Data 055 | 1 | INT16U | R | N | ---
|  |  | 5182 | Command Data 056 | 1 | INT16U | R | N | ---
|  |  | 5183 | Command Data 057 | 1 | INT16U | R | N | ---
|  |  | 5184 | Command Data 058 | 1 | INT16U | R | N | ---
|  |  | 5185 | Command Data 059 | 1 | INT16U | R | N | ---
|  |  | 5186 | Command Data 060 | 1 | INT16U | R | N | ---
|  |  | 5187 | Command Data 061 | 1 | INT16U | R | N | ---
|  |  | 5188 | Command Data 062 | 1 | INT16U | R | N | ---
|  |  | 5189 | Command Data 063 | 1 | INT16U | R | N | ---
|  |  | 5190 | Command Data 064 | 1 | INT16U | R | N | ---
|  |  | 5191 | Command Data 065 | 1 | INT16U | R | N | ---
|  |  | 5192 | Command Data 066 | 1 | INT16U | R | N | ---
|  |  | 5193 | Command Data 067 | 1 | INT16U | R | N | ---
|  |  | 5194 | Command Data 068 | 1 | INT16U | R | N | ---
|  |  | 5195 | Command Data 069 | 1 | INT16U | R | N | ---
|  |  | 5196 | Command Data 070 | 1 | INT16U | R | N | ---
|  |  | 5197 | Command Data 071 | 1 | INT16U | R | N | ---
|  |  | 5198 | Command Data 072 | 1 | INT16U | R | N | ---
|  |  | 5199 | Command Data 073 | 1 | INT16U | R | N | ---
|  |  | 5200 | Command Data 074 | 1 | INT16U | R | N | ---
|  |  | 5201 | Command Data 075 | 1 | INT16U | R | N | ---
|  |  | 5202 | Command Data 076 | 1 | INT16U | R | N | ---
|  |  | 5203 | Command Data 077 | 1 | INT16U | R | N | ---
|  |  | 5204 | Command Data 078 | 1 | INT16U | R | N | ---
|  |  | 5205 | Command Data 079 | 1 | INT16U | R | N | ---
|  |  | 5206 | Command Data 080 | 1 | INT16U | R | N | ---
|  |  | 5207 | Command Data 081 | 1 | INT16U | R | N | ---
|  |  | 5208 | Command Data 082 | 1 | INT16U | R | N | ---
|  |  | 5209 | Command Data 083 | 1 | INT16U | R | N | ---
|  |  | 5210 | Command Data 084 | 1 | INT16U | R | N | ---
|  |  | 5211 | Command Data 085 | 1 | INT16U | R | N | ---
|  |  | 5212 | Command Data 086 | 1 | INT16U | R | N | ---
|  |  | 5213 | Command Data 087 | 1 | INT16U | R | N | ---
|  |  | 5214 | Command Data 088 | 1 | INT16U | R | N | ---
|  |  | 5215 | Command Data 089 | 1 | INT16U | R | N | ---
|  |  | 5216 | Command Data 090 | 1 | INT16U | R | N | ---
|  |  | 5217 | Command Data 091 | 1 | INT16U | R | N | ---
|  |  | 5218 | Command Data 092 | 1 | INT16U | R | N | ---
|  |  | 5219 | Command Data 093 | 1 | INT16U | R | N | ---
|  |  | 5220 | Command Data 094 | 1 | INT16U | R | N | ---
|  |  | 5221 | Command Data 095 | 1 | INT16U | R | N | ---
|  |  | 5222 | Command Data 096 | 1 | INT16U | R | N | ---
|  |  | 5223 | Command Data 097 | 1 | INT16U | R | N | ---
|  |  | 5224 | Command Data 098 | 1 | INT16U | R | N | ---
|  |  | 5225 | Command Data 099 | 1 | INT16U | R | N | ---
|  |  | 5226 | Command Data 100 | 1 | INT16U | R | N | ---
|  |  | 5227 | Command Data 101 | 1 | INT16U | R | N | ---
|  |  | 5228 | Command Data 102 | 1 | INT16U | R | N | ---
|  |  | 5229 | Command Data 103 | 1 | INT16U | R | N | ---
|  |  | 5230 | Command Data 104 | 1 | INT16U | R | N | ---
|  |  | 5231 | Command Data 105 | 1 | INT16U | R | N | ---
|  |  | 5232 | Command Data 106 | 1 | INT16U | R | N | ---
|  |  | 5233 | Command Data 107 | 1 | INT16U | R | N | ---
|  |  | 5234 | Command Data 108 | 1 | INT16U | R | N | ---
|  |  | 5235 | Command Data 109 | 1 | INT16U | R | N | ---
|  |  | 5236 | Command Data 110 | 1 | INT16U | R | N | ---
|  |  | 5237 | Command Data 111 | 1 | INT16U | R | N | ---
|  |  | 5238 | Command Data 112 | 1 | INT16U | R | N | ---
|  |  | 5239 | Command Data 113 | 1 | INT16U | R | N | ---
|  |  | 5240 | Command Data 114 | 1 | INT16U | R | N | ---
|  |  | 5241 | Command Data 115 | 1 | INT16U | R | N | ---
|  |  | 5242 | Command Data 116 | 1 | INT16U | R | N | ---
|  |  | 5243 | Command Data 117 | 1 | INT16U | R | N | ---
|  |  | 5244 | Command Data 118 | 1 | INT16U | R | N | ---
|  |  | 5245 | Command Data 119 | 1 | INT16U | R | N | ---
|  |  | 5246 | Command Data 120 | 1 | INT16U | R | N | ---
|  |  | 5247 | Command Data 121 | 1 | INT16U | R | N | ---
|  |  | 5248 | Command Data 122 | 1 | INT16U | R | N | ---
|  |  | 5249 | Command Data 123 | 1 | INT16U | R | N | ---
Unprotected Command Interface
Command parameters
|  |  | 5250 | Requested Command | 1 | INT16U | RW | N | ---
|  |  | 5252 | Command Parameter 001 | 1 | INT16U | RW | N | ---
|  |  | 5253 | Command Parameter 002 | 1 | INT16U | RW | N | ---
|  |  | 5254 | Command Parameter 003 | 1 | INT16U | RW | N | ---
|  |  | 5255 | Command Parameter 004 | 1 | INT16U | RW | N | ---
|  |  | 5256 | Command Parameter 005 | 1 | INT16U | RW | N | ---
|  |  | 5257 | Command Parameter 006 | 1 | INT16U | RW | N | ---
|  |  | 5258 | Command Parameter 007 | 1 | INT16U | RW | N | ---
|  |  | 5259 | Command Parameter 008 | 1 | INT16U | RW | N | ---
|  |  | 5260 | Command Parameter 009 | 1 | INT16U | RW | N | ---
|  |  | 5261 | Command Parameter 010 | 1 | INT16U | RW | N | ---
|  |  | 5262 | Command Parameter 011 | 1 | INT16U | RW | N | ---
|  |  | 5263 | Command Parameter 012 | 1 | INT16U | RW | N | ---
|  |  | 5264 | Command Parameter 013 | 1 | INT16U | RW | N | ---
|  |  | 5265 | Command Parameter 014 | 1 | INT16U | RW | N | ---
|  |  | 5266 | Command Parameter 015 | 1 | INT16U | RW | N | ---
|  |  | 5267 | Command Parameter 016 | 1 | INT16U | RW | N | ---
|  |  | 5268 | Command Parameter 017 | 1 | INT16U | RW | N | ---
|  |  | 5269 | Command Parameter 018 | 1 | INT16U | RW | N | ---
|  |  | 5270 | Command Parameter 019 | 1 | INT16U | RW | N | ---
|  |  | 5271 | Command Parameter 020 | 1 | INT16U | RW | N | ---
|  |  | 5272 | Command Parameter 021 | 1 | INT16U | RW | N | ---
|  |  | 5273 | Command Parameter 022 | 1 | INT16U | RW | N | ---
|  |  | 5274 | Command Parameter 023 | 1 | INT16U | RW | N | ---
|  |  | 5275 | Command Parameter 024 | 1 | INT16U | RW | N | ---
|  |  | 5276 | Command Parameter 025 | 1 | INT16U | RW | N | ---
|  |  | 5277 | Command Parameter 026 | 1 | INT16U | RW | N | ---
|  |  | 5278 | Command Parameter 027 | 1 | INT16U | RW | N | ---
|  |  | 5279 | Command Parameter 028 | 1 | INT16U | RW | N | ---
|  |  | 5280 | Command Parameter 029 | 1 | INT16U | RW | N | ---
|  |  | 5281 | Command Parameter 030 | 1 | INT16U | RW | N | ---
|  |  | 5282 | Command Parameter 031 | 1 | INT16U | RW | N | ---
|  |  | 5283 | Command Parameter 032 | 1 | INT16U | RW | N | ---
|  |  | 5284 | Command Parameter 033 | 1 | INT16U | RW | N | ---
|  |  | 5285 | Command Parameter 034 | 1 | INT16U | RW | N | ---
|  |  | 5286 | Command Parameter 035 | 1 | INT16U | RW | N | ---
|  |  | 5287 | Command Parameter 036 | 1 | INT16U | RW | N | ---
|  |  | 5288 | Command Parameter 037 | 1 | INT16U | RW | N | ---
|  |  | 5289 | Command Parameter 038 | 1 | INT16U | RW | N | ---
|  |  | 5290 | Command Parameter 039 | 1 | INT16U | RW | N | ---
|  |  | 5291 | Command Parameter 040 | 1 | INT16U | RW | N | ---
|  |  | 5292 | Command Parameter 041 | 1 | INT16U | RW | N | ---
|  |  | 5293 | Command Parameter 042 | 1 | INT16U | RW | N | ---
|  |  | 5294 | Command Parameter 043 | 1 | INT16U | RW | N | ---
|  |  | 5295 | Command Parameter 044 | 1 | INT16U | RW | N | ---
|  |  | 5296 | Command Parameter 045 | 1 | INT16U | RW | N | ---
|  |  | 5297 | Command Parameter 046 | 1 | INT16U | RW | N | ---
|  |  | 5298 | Command Parameter 047 | 1 | INT16U | RW | N | ---
|  |  | 5299 | Command Parameter 048 | 1 | INT16U | RW | N | ---
|  |  | 5300 | Command Parameter 049 | 1 | INT16U | RW | N | ---
|  |  | 5301 | Command Parameter 050 | 1 | INT16U | RW | N | ---
|  |  | 5302 | Command Parameter 051 | 1 | INT16U | RW | N | ---
|  |  | 5303 | Command Parameter 052 | 1 | INT16U | RW | N | ---
|  |  | 5304 | Command Parameter 053 | 1 | INT16U | RW | N | ---
|  |  | 5305 | Command Parameter 054 | 1 | INT16U | RW | N | ---
|  |  | 5306 | Command Parameter 055 | 1 | INT16U | RW | N | ---
|  |  | 5307 | Command Parameter 056 | 1 | INT16U | RW | N | ---
|  |  | 5308 | Command Parameter 057 | 1 | INT16U | RW | N | ---
|  |  | 5309 | Command Parameter 058 | 1 | INT16U | RW | N | ---
|  |  | 5310 | Command Parameter 059 | 1 | INT16U | RW | N | ---
|  |  | 5311 | Command Parameter 060 | 1 | INT16U | RW | N | ---
|  |  | 5312 | Command Parameter 061 | 1 | INT16U | RW | N | ---
|  |  | 5313 | Command Parameter 062 | 1 | INT16U | RW | N | ---
|  |  | 5314 | Command Parameter 063 | 1 | INT16U | RW | N | ---
|  |  | 5315 | Command Parameter 064 | 1 | INT16U | RW | N | ---
|  |  | 5316 | Command Parameter 065 | 1 | INT16U | RW | N | ---
|  |  | 5317 | Command Parameter 066 | 1 | INT16U | RW | N | ---
|  |  | 5318 | Command Parameter 067 | 1 | INT16U | RW | N | ---
|  |  | 5319 | Command Parameter 068 | 1 | INT16U | RW | N | ---
|  |  | 5320 | Command Parameter 069 | 1 | INT16U | RW | N | ---
|  |  | 5321 | Command Parameter 070 | 1 | INT16U | RW | N | ---
|  |  | 5322 | Command Parameter 071 | 1 | INT16U | RW | N | ---
|  |  | 5323 | Command Parameter 072 | 1 | INT16U | RW | N | ---
|  |  | 5324 | Command Parameter 073 | 1 | INT16U | RW | N | ---
|  |  | 5325 | Command Parameter 074 | 1 | INT16U | RW | N | ---
|  |  | 5326 | Command Parameter 075 | 1 | INT16U | RW | N | ---
|  |  | 5327 | Command Parameter 076 | 1 | INT16U | RW | N | ---
|  |  | 5328 | Command Parameter 077 | 1 | INT16U | RW | N | ---
|  |  | 5329 | Command Parameter 078 | 1 | INT16U | RW | N | ---
|  |  | 5330 | Command Parameter 079 | 1 | INT16U | RW | N | ---
|  |  | 5331 | Command Parameter 080 | 1 | INT16U | RW | N | ---
|  |  | 5332 | Command Parameter 081 | 1 | INT16U | RW | N | ---
|  |  | 5333 | Command Parameter 082 | 1 | INT16U | RW | N | ---
|  |  | 5334 | Command Parameter 083 | 1 | INT16U | RW | N | ---
|  |  | 5335 | Command Parameter 084 | 1 | INT16U | RW | N | ---
|  |  | 5336 | Command Parameter 085 | 1 | INT16U | RW | N | ---
|  |  | 5337 | Command Parameter 086 | 1 | INT16U | RW | N | ---
|  |  | 5338 | Command Parameter 087 | 1 | INT16U | RW | N | ---
|  |  | 5339 | Command Parameter 088 | 1 | INT16U | RW | N | ---
|  |  | 5340 | Command Parameter 089 | 1 | INT16U | RW | N | ---
|  |  | 5341 | Command Parameter 090 | 1 | INT16U | RW | N | ---
|  |  | 5342 | Command Parameter 091 | 1 | INT16U | RW | N | ---
|  |  | 5343 | Command Parameter 092 | 1 | INT16U | RW | N | ---
|  |  | 5344 | Command Parameter 093 | 1 | INT16U | RW | N | ---
|  |  | 5345 | Command Parameter 094 | 1 | INT16U | RW | N | ---
|  |  | 5346 | Command Parameter 095 | 1 | INT16U | RW | N | ---
|  |  | 5347 | Command Parameter 096 | 1 | INT16U | RW | N | ---
|  |  | 5348 | Command Parameter 097 | 1 | INT16U | RW | N | ---
|  |  | 5349 | Command Parameter 098 | 1 | INT16U | RW | N | ---
|  |  | 5350 | Command Parameter 099 | 1 | INT16U | RW | N | ---
|  |  | 5351 | Command Parameter 100 | 1 | INT16U | RW | N | ---
|  |  | 5352 | Command Parameter 101 | 1 | INT16U | RW | N | ---
|  |  | 5353 | Command Parameter 102 | 1 | INT16U | RW | N | ---
|  |  | 5354 | Command Parameter 103 | 1 | INT16U | RW | N | ---
|  |  | 5355 | Command Parameter 104 | 1 | INT16U | RW | N | ---
|  |  | 5356 | Command Parameter 105 | 1 | INT16U | RW | N | ---
|  |  | 5357 | Command Parameter 106 | 1 | INT16U | RW | N | ---
|  |  | 5358 | Command Parameter 107 | 1 | INT16U | RW | N | ---
|  |  | 5359 | Command Parameter 108 | 1 | INT16U | RW | N | ---
|  |  | 5360 | Command Parameter 109 | 1 | INT16U | RW | N | ---
|  |  | 5361 | Command Parameter 110 | 1 | INT16U | RW | N | ---
|  |  | 5362 | Command Parameter 111 | 1 | INT16U | RW | N | ---
|  |  | 5363 | Command Parameter 112 | 1 | INT16U | RW | N | ---
|  |  | 5364 | Command Parameter 113 | 1 | INT16U | RW | N | ---
|  |  | 5365 | Command Parameter 114 | 1 | INT16U | RW | N | ---
|  |  | 5366 | Command Parameter 115 | 1 | INT16U | RW | N | ---
|  |  | 5367 | Command Parameter 116 | 1 | INT16U | RW | N | ---
|  |  | 5368 | Command Parameter 117 | 1 | INT16U | RW | N | ---
|  |  | 5369 | Command Parameter 118 | 1 | INT16U | RW | N | ---
|  |  | 5370 | Command Parameter 119 | 1 | INT16U | RW | N | ---
|  |  | 5371 | Command Parameter 120 | 1 | INT16U | RW | N | ---
|  |  | 5372 | Command Parameter 121 | 1 | INT16U | RW | N | ---
|  |  | 5373 | Command Parameter 122 | 1 | INT16U | RW | N | ---
|  |  | 5374 | Command Parameter 123 | 1 | INT16U | RW | N | ---
|  |  | 5375 | Command Status | 1 | INT16U | R | N | ---
|  |  | 5376 | Command Result | 1 | INT16U | R | N | ---
|  |  | 5377 | Command Data 001 | 1 | INT16U | R | N | ---
|  |  | 5378 | Command Data 002 | 1 | INT16U | R | N | ---
|  |  | 5379 | Command Data 003 | 1 | INT16U | R | N | ---
|  |  | 5380 | Command Data 004 | 1 | INT16U | R | N | ---
|  |  | 5381 | Command Data 005 | 1 | INT16U | R | N | ---
|  |  | 5382 | Command Data 006 | 1 | INT16U | R | N | ---
|  |  | 5383 | Command Data 007 | 1 | INT16U | R | N | ---
|  |  | 5384 | Command Data 008 | 1 | INT16U | R | N | ---
|  |  | 5385 | Command Data 009 | 1 | INT16U | R | N | ---
|  |  | 5386 | Command Data 010 | 1 | INT16U | R | N | ---
|  |  | 5387 | Command Data 011 | 1 | INT16U | R | N | ---
|  |  | 5388 | Command Data 012 | 1 | INT16U | R | N | ---
|  |  | 5389 | Command Data 013 | 1 | INT16U | R | N | ---
|  |  | 5390 | Command Data 014 | 1 | INT16U | R | N | ---
|  |  | 5391 | Command Data 015 | 1 | INT16U | R | N | ---
|  |  | 5392 | Command Data 016 | 1 | INT16U | R | N | ---
|  |  | 5393 | Command Data 017 | 1 | INT16U | R | N | ---
|  |  | 5394 | Command Data 018 | 1 | INT16U | R | N | ---
|  |  | 5395 | Command Data 019 | 1 | INT16U | R | N | ---
|  |  | 5396 | Command Data 020 | 1 | INT16U | R | N | ---
|  |  | 5397 | Command Data 021 | 1 | INT16U | R | N | ---
|  |  | 5398 | Command Data 022 | 1 | INT16U | R | N | ---
|  |  | 5399 | Command Data 023 | 1 | INT16U | R | N | ---
|  |  | 5400 | Command Data 024 | 1 | INT16U | R | N | ---
|  |  | 5401 | Command Data 025 | 1 | INT16U | R | N | ---
|  |  | 5402 | Command Data 026 | 1 | INT16U | R | N | ---
|  |  | 5403 | Command Data 027 | 1 | INT16U | R | N | ---
|  |  | 5404 | Command Data 028 | 1 | INT16U | R | N | ---
|  |  | 5405 | Command Data 029 | 1 | INT16U | R | N | ---
|  |  | 5406 | Command Data 030 | 1 | INT16U | R | N | ---
|  |  | 5407 | Command Data 031 | 1 | INT16U | R | N | ---
|  |  | 5408 | Command Data 032 | 1 | INT16U | R | N | ---
|  |  | 5409 | Command Data 033 | 1 | INT16U | R | N | ---
|  |  | 5410 | Command Data 034 | 1 | INT16U | R | N | ---
|  |  | 5411 | Command Data 035 | 1 | INT16U | R | N | ---
|  |  | 5412 | Command Data 036 | 1 | INT16U | R | N | ---
|  |  | 5413 | Command Data 037 | 1 | INT16U | R | N | ---
|  |  | 5414 | Command Data 038 | 1 | INT16U | R | N | ---
|  |  | 5415 | Command Data 039 | 1 | INT16U | R | N | ---
|  |  | 5416 | Command Data 040 | 1 | INT16U | R | N | ---
|  |  | 5417 | Command Data 041 | 1 | INT16U | R | N | ---
|  |  | 5418 | Command Data 042 | 1 | INT16U | R | N | ---
|  |  | 5419 | Command Data 043 | 1 | INT16U | R | N | ---
|  |  | 5420 | Command Data 044 | 1 | INT16U | R | N | ---
|  |  | 5421 | Command Data 045 | 1 | INT16U | R | N | ---
|  |  | 5422 | Command Data 046 | 1 | INT16U | R | N | ---
|  |  | 5423 | Command Data 047 | 1 | INT16U | R | N | ---
|  |  | 5424 | Command Data 048 | 1 | INT16U | R | N | ---
|  |  | 5425 | Command Data 049 | 1 | INT16U | R | N | ---
|  |  | 5426 | Command Data 050 | 1 | INT16U | R | N | ---
|  |  | 5427 | Command Data 051 | 1 | INT16U | R | N | ---
|  |  | 5428 | Command Data 052 | 1 | INT16U | R | N | ---
|  |  | 5429 | Command Data 053 | 1 | INT16U | R | N | ---
|  |  | 5430 | Command Data 054 | 1 | INT16U | R | N | ---
|  |  | 5431 | Command Data 055 | 1 | INT16U | R | N | ---
|  |  | 5432 | Command Data 056 | 1 | INT16U | R | N | ---
|  |  | 5433 | Command Data 057 | 1 | INT16U | R | N | ---
|  |  | 5434 | Command Data 058 | 1 | INT16U | R | N | ---
|  |  | 5435 | Command Data 059 | 1 | INT16U | R | N | ---
|  |  | 5436 | Command Data 060 | 1 | INT16U | R | N | ---
|  |  | 5437 | Command Data 061 | 1 | INT16U | R | N | ---
|  |  | 5438 | Command Data 062 | 1 | INT16U | R | N | ---
|  |  | 5439 | Command Data 063 | 1 | INT16U | R | N | ---
|  |  | 5440 | Command Data 064 | 1 | INT16U | R | N | ---
|  |  | 5441 | Command Data 065 | 1 | INT16U | R | N | ---
|  |  | 5442 | Command Data 066 | 1 | INT16U | R | N | ---
|  |  | 5443 | Command Data 067 | 1 | INT16U | R | N | ---
|  |  | 5444 | Command Data 068 | 1 | INT16U | R | N | ---
|  |  | 5445 | Command Data 069 | 1 | INT16U | R | N | ---
|  |  | 5446 | Command Data 070 | 1 | INT16U | R | N | ---
|  |  | 5447 | Command Data 071 | 1 | INT16U | R | N | ---
|  |  | 5448 | Command Data 072 | 1 | INT16U | R | N | ---
|  |  | 5449 | Command Data 073 | 1 | INT16U | R | N | ---
|  |  | 5450 | Command Data 074 | 1 | INT16U | R | N | ---
|  |  | 5451 | Command Data 075 | 1 | INT16U | R | N | ---
|  |  | 5452 | Command Data 076 | 1 | INT16U | R | N | ---
|  |  | 5453 | Command Data 077 | 1 | INT16U | R | N | ---
|  |  | 5454 | Command Data 078 | 1 | INT16U | R | N | ---
|  |  | 5455 | Command Data 079 | 1 | INT16U | R | N | ---
|  |  | 5456 | Command Data 080 | 1 | INT16U | R | N | ---
|  |  | 5457 | Command Data 081 | 1 | INT16U | R | N | ---
|  |  | 5458 | Command Data 082 | 1 | INT16U | R | N | ---
|  |  | 5459 | Command Data 083 | 1 | INT16U | R | N | ---
|  |  | 5460 | Command Data 084 | 1 | INT16U | R | N | ---
|  |  | 5461 | Command Data 085 | 1 | INT16U | R | N | ---
|  |  | 5462 | Command Data 086 | 1 | INT16U | R | N | ---
|  |  | 5463 | Command Data 087 | 1 | INT16U | R | N | ---
|  |  | 5464 | Command Data 088 | 1 | INT16U | R | N | ---
|  |  | 5465 | Command Data 089 | 1 | INT16U | R | N | ---
|  |  | 5466 | Command Data 090 | 1 | INT16U | R | N | ---
|  |  | 5467 | Command Data 091 | 1 | INT16U | R | N | ---
|  |  | 5468 | Command Data 092 | 1 | INT16U | R | N | ---
|  |  | 5469 | Command Data 093 | 1 | INT16U | R | N | ---
|  |  | 5470 | Command Data 094 | 1 | INT16U | R | N | ---
|  |  | 5471 | Command Data 095 | 1 | INT16U | R | N | ---
|  |  | 5472 | Command Data 096 | 1 | INT16U | R | N | ---
|  |  | 5473 | Command Data 097 | 1 | INT16U | R | N | ---
|  |  | 5474 | Command Data 098 | 1 | INT16U | R | N | ---
|  |  | 5475 | Command Data 099 | 1 | INT16U | R | N | ---
|  |  | 5476 | Command Data 100 | 1 | INT16U | R | N | ---
|  |  | 5477 | Command Data 101 | 1 | INT16U | R | N | ---
|  |  | 5478 | Command Data 102 | 1 | INT16U | R | N | ---
|  |  | 5479 | Command Data 103 | 1 | INT16U | R | N | ---
|  |  | 5480 | Command Data 104 | 1 | INT16U | R | N | ---
|  |  | 5481 | Command Data 105 | 1 | INT16U | R | N | ---
|  |  | 5482 | Command Data 106 | 1 | INT16U | R | N | ---
|  |  | 5483 | Command Data 107 | 1 | INT16U | R | N | ---
|  |  | 5484 | Command Data 108 | 1 | INT16U | R | N | ---
|  |  | 5485 | Command Data 109 | 1 | INT16U | R | N | ---
|  |  | 5486 | Command Data 110 | 1 | INT16U | R | N | ---
|  |  | 5487 | Command Data 111 | 1 | INT16U | R | N | ---
|  |  | 5488 | Command Data 112 | 1 | INT16U | R | N | ---
|  |  | 5489 | Command Data 113 | 1 | INT16U | R | N | ---
|  |  | 5490 | Command Data 114 | 1 | INT16U | R | N | ---
|  |  | 5491 | Command Data 115 | 1 | INT16U | R | N | ---
|  |  | 5492 | Command Data 116 | 1 | INT16U | R | N | ---
|  |  | 5493 | Command Data 117 | 1 | INT16U | R | N | ---
|  |  | 5494 | Command Data 118 | 1 | INT16U | R | N | ---
|  |  | 5495 | Command Data 119 | 1 | INT16U | R | N | ---
|  |  | 5496 | Command Data 120 | 1 | INT16U | R | N | ---
|  |  | 5497 | Command Data 121 | 1 | INT16U | R | N | ---
|  |  | 5498 | Command Data 122 | 1 | INT16U | R | N | ---
|  |  | 5499 | Command Data 123 | 1 | INT16U | R | N | ---
Mailbox Registers
|  |  | 5580 | Mailbox Register 001 | 1 | INT16U | RW | Y | ---
|  |  | 5581 | Mailbox Register 002 | 1 | INT16U | RW | Y | ---
|  |  | 5582 | Mailbox Register 003 | 1 | INT16U | RW | Y | ---
|  |  | 5583 | Mailbox Register 004 | 1 | INT16U | RW | Y | ---
|  |  | 5584 | Mailbox Register 005 | 1 | INT16U | RW | Y | ---
|  |  | 5585 | Mailbox Register 006 | 1 | INT16U | RW | Y | ---
|  |  | 5586 | Mailbox Register 007 | 1 | INT16U | RW | Y | ---
|  |  | 5587 | Mailbox Register 008 | 1 | INT16U | RW | Y | ---
|  |  | 5588 | Mailbox Register 009 | 1 | INT16U | RW | Y | ---
|  |  | 5589 | Mailbox Register 010 | 1 | INT16U | RW | Y | ---
|  |  | 5590 | Mailbox Register 011 | 1 | INT16U | RW | Y | ---
|  |  | 5591 | Mailbox Register 012 | 1 | INT16U | RW | Y | ---
|  |  | 5592 | Mailbox Register 013 | 1 | INT16U | RW | Y | ---
|  |  | 5593 | Mailbox Register 014 | 1 | INT16U | RW | Y | ---
|  |  | 5594 | Mailbox Register 015 | 1 | INT16U | RW | Y | ---
|  |  | 5595 | Mailbox Register 016 | 1 | INT16U | RW | Y | ---
|  |  | 5596 | Mailbox Register 017 | 1 | INT16U | RW | Y | ---
|  |  | 5597 | Mailbox Register 018 | 1 | INT16U | RW | Y | ---
|  |  | 5598 | Mailbox Register 019 | 1 | INT16U | RW | Y | ---
|  |  | 5599 | Mailbox Register 020 | 1 | INT16U | RW | Y | ---
|  |  | 5600 | Mailbox Register 021 | 1 | INT16U | RW | Y | ---
|  |  | 5601 | Mailbox Register 022 | 1 | INT16U | RW | Y | ---
|  |  | 5602 | Mailbox Register 023 | 1 | INT16U | RW | Y | ---
|  |  | 5603 | Mailbox Register 024 | 1 | INT16U | RW | Y | ---
|  |  | 5604 | Mailbox Register 025 | 1 | INT16U | RW | Y | ---
|  |  | 5605 | Mailbox Register 026 | 1 | INT16U | RW | Y | ---
|  |  | 5606 | Mailbox Register 027 | 1 | INT16U | RW | Y | ---
|  |  | 5607 | Mailbox Register 028 | 1 | INT16U | RW | Y | ---
|  |  | 5608 | Mailbox Register 029 | 1 | INT16U | RW | Y | ---
|  |  | 5609 | Mailbox Register 030 | 1 | INT16U | RW | Y | ---
|  |  | 5610 | Mailbox Register 031 | 1 | INT16U | RW | Y | ---
|  |  | 5611 | Mailbox Register 032 | 1 | INT16U | RW | Y | ---
|  |  | 5612 | Mailbox Register 033 | 1 | INT16U | RW | Y | ---
|  |  | 5613 | Mailbox Register 034 | 1 | INT16U | RW | Y | ---
|  |  | 5614 | Mailbox Register 035 | 1 | INT16U | RW | Y | ---
|  |  | 5615 | Mailbox Register 036 | 1 | INT16U | RW | Y | ---
|  |  | 5616 | Mailbox Register 037 | 1 | INT16U | RW | Y | ---
|  |  | 5617 | Mailbox Register 038 | 1 | INT16U | RW | Y | ---
|  |  | 5618 | Mailbox Register 039 | 1 | INT16U | RW | Y | ---
|  |  | 5619 | Mailbox Register 040 | 1 | INT16U | RW | Y | ---
|  |  | 5620 | Mailbox Register 041 | 1 | INT16U | RW | Y | ---
|  |  | 5621 | Mailbox Register 042 | 1 | INT16U | RW | Y | ---
|  |  | 5622 | Mailbox Register 043 | 1 | INT16U | RW | Y | ---
|  |  | 5623 | Mailbox Register 044 | 1 | INT16U | RW | Y | ---
|  |  | 5624 | Mailbox Register 045 | 1 | INT16U | RW | Y | ---
|  |  | 5625 | Mailbox Register 046 | 1 | INT16U | RW | Y | ---
|  |  | 5626 | Mailbox Register 047 | 1 | INT16U | RW | Y | ---
|  |  | 5627 | Mailbox Register 048 | 1 | INT16U | RW | Y | ---
|  |  | 5628 | Mailbox Register 049 | 1 | INT16U | RW | Y | ---
|  |  | 5629 | Mailbox Register 050 | 1 | INT16U | RW | Y | ---
|  |  | 5630 | Mailbox Register 051 | 1 | INT16U | RW | Y | ---
|  |  | 5631 | Mailbox Register 052 | 1 | INT16U | RW | Y | ---
|  |  | 5632 | Mailbox Register 053 | 1 | INT16U | RW | Y | ---
|  |  | 5633 | Mailbox Register 054 | 1 | INT16U | RW | Y | ---
|  |  | 5634 | Mailbox Register 055 | 1 | INT16U | RW | Y | ---
|  |  | 5635 | Mailbox Register 056 | 1 | INT16U | RW | Y | ---
|  |  | 5636 | Mailbox Register 057 | 1 | INT16U | RW | Y | ---
|  |  | 5637 | Mailbox Register 058 | 1 | INT16U | RW | Y | ---
|  |  | 5638 | Mailbox Register 059 | 1 | INT16U | RW | Y | ---
|  |  | 5639 | Mailbox Register 060 | 1 | INT16U | RW | Y | ---
|  |  | 5640 | Mailbox Register 061 | 1 | INT16U | RW | Y | ---
|  |  | 5641 | Mailbox Register 062 | 1 | INT16U | RW | Y | ---
|  |  | 5642 | Mailbox Register 063 | 1 | INT16U | RW | Y | ---
|  |  | 5643 | Mailbox Register 064 | 1 | INT16U | RW | Y | ---
|  |  | 5644 | Mailbox Register 065 | 1 | INT16U | RW | Y | ---
|  |  | 5645 | Mailbox Register 066 | 1 | INT16U | RW | Y | ---
|  |  | 5646 | Mailbox Register 067 | 1 | INT16U | RW | Y | ---
|  |  | 5647 | Mailbox Register 068 | 1 | INT16U | RW | Y | ---
|  |  | 5648 | Mailbox Register 069 | 1 | INT16U | RW | Y | ---
|  |  | 5649 | Mailbox Register 070 | 1 | INT16U | RW | Y | ---
|  |  | 5650 | Mailbox Register 071 | 1 | INT16U | RW | Y | ---
|  |  | 5651 | Mailbox Register 072 | 1 | INT16U | RW | Y | ---
|  |  | 5652 | Mailbox Register 073 | 1 | INT16U | RW | Y | ---
|  |  | 5653 | Mailbox Register 074 | 1 | INT16U | RW | Y | ---
|  |  | 5654 | Mailbox Register 075 | 1 | INT16U | RW | Y | ---
|  |  | 5655 | Mailbox Register 076 | 1 | INT16U | RW | Y | ---
|  |  | 5656 | Mailbox Register 077 | 1 | INT16U | RW | Y | ---
|  |  | 5657 | Mailbox Register 078 | 1 | INT16U | RW | Y | ---
|  |  | 5658 | Mailbox Register 079 | 1 | INT16U | RW | Y | ---
|  |  | 5659 | Mailbox Register 080 | 1 | INT16U | RW | Y | ---
|  |  | 5660 | Mailbox Register 081 | 1 | INT16U | RW | Y | ---
|  |  | 5661 | Mailbox Register 082 | 1 | INT16U | RW | Y | ---
|  |  | 5662 | Mailbox Register 083 | 1 | INT16U | RW | Y | ---
|  |  | 5663 | Mailbox Register 084 | 1 | INT16U | RW | Y | ---
|  |  | 5664 | Mailbox Register 085 | 1 | INT16U | RW | Y | ---
|  |  | 5665 | Mailbox Register 086 | 1 | INT16U | RW | Y | ---
|  |  | 5666 | Mailbox Register 087 | 1 | INT16U | RW | Y | ---
|  |  | 5667 | Mailbox Register 088 | 1 | INT16U | RW | Y | ---
|  |  | 5668 | Mailbox Register 089 | 1 | INT16U | RW | Y | ---
|  |  | 5669 | Mailbox Register 090 | 1 | INT16U | RW | Y | ---
|  |  | 5670 | Mailbox Register 091 | 1 | INT16U | RW | Y | ---
|  |  | 5671 | Mailbox Register 092 | 1 | INT16U | RW | Y | ---
|  |  | 5672 | Mailbox Register 093 | 1 | INT16U | RW | Y | ---
|  |  | 5673 | Mailbox Register 094 | 1 | INT16U | RW | Y | ---
|  |  | 5674 | Mailbox Register 095 | 1 | INT16U | RW | Y | ---
|  |  | 5675 | Mailbox Register 096 | 1 | INT16U | RW | Y | ---
|  |  | 5676 | Mailbox Register 097 | 1 | INT16U | RW | Y | ---
|  |  | 5677 | Mailbox Register 098 | 1 | INT16U | RW | Y | ---
|  |  | 5678 | Mailbox Register 099 | 1 | INT16U | RW | Y | ---
|  |  | 5679 | Mailbox Register 100 | 1 | INT16U | RW | Y | ---
Command Semaphore
|  |  | 5680 |  | 1 | INT16U | RW | N | ---
HMI
Setup
Basic HMI Setup
|  |  | 6001 | HMI Contrast Setting | 1 | INT16U | RWC | Y | --- | 1 = Brightest…9 = Dimmest
|  |  | 6003 | HMI Language | 1 | INT16U | RWC | Y | --- | 0 = EnglishUS 1 = EnglishUK 2 = French 3 = Spanish 4 = German 5 = Italian 6 = Polish 7 = Portuguese 8 = Turkish 9 = Chinese 10 = Russian 11 = Arabic 12 = Dutch
|  |  | 6004 | HMI Date Format | 1 | INT16U | RWC | Y | --- | 0 = MM/DD/YYYY 1 = YYYY/MM/DD 2 = DD/MM/YYYY
|  |  | 6005 | HMI Time Format | 1 | INT16U | RWC | Y | --- | 0 = 2400hr 1 = AM/PM
|  |  | 6006 | HMI IEC/IEEE Mode | 1 | INT16U | RWC | Y | --- | 0 = IEC 1 = IEEE
|  |  | 6007 | HMI Screen Timeout | 1 | INT16U | RWC | Y | minutes | 0 = disabled
|  |  | 6008 | HMI Backlight Timeout | 1 | INT16U | RWC | Y | minutes | 0 = disabled
Communications
RS-485
RS-485 Base Unit
|  |  | 6500 | RS-485 Comm Port (M/S) Protocol | 1 | INT16U | RWC | Y | --- | 0 = Modbus 1 = Jbus 2 = Modbus ASCII 8-Bit 3 = Modbus ASCII 7-Bit
|  |  | 6501 | RS-485 Comm Port (M/S) Address | 1 | INT16U | RWC | Y | --- | Valid Addresses: Modbus: 1 – 247 Jbus: 1 – 255
|  |  | 6502 | RS-485 Comm Port (M/S) Baud Rate | 1 | INT16U | RWC | Y | --- | 0 = 9600 1 = 19200 2 = 38400
|  |  | 6503 | RS-485 Comm Port (M/S) Parity | 1 | INT16U | RWC | Y | --- | 0 = Even 1 = Odd 2 = None
|  |  | 6504 | RS-485 Comm Port (M/S) Modbus ASCII Default Timeout | 1 | INT16U | RWC | Y | msec | Timeout for end of ASCII packet when no control delimitation is detected.
|  |  | 6508 | RS-485 Comm Port (M/S) Packets To This Unit | 1 | INT16U | R | Y | --- | Number of valid messages addressed to this unit
|  |  | 6509 | RS-485 Comm Port (S) Packets To Other Units | 1 | INT16U | R | Y | --- | Number of valid messages addressed to other units
|  |  | 6510 | RS-485 Comm Port (M/S) Packets With Bad CRC | 1 | INT16U | R | Y | --- | Number of messages received with bad CRC
|  |  | 6511 | RS-485 Comm Port (M/S) Packets With Error | 1 | INT16U | R | Y | --- | Number of messages received with errors
|  |  | 6512 | RS-485 Comm Port (M/S) Packets With Illegal Opcode | 1 | INT16U | R | Y | --- | Number of messages received with an illegal opcode
|  |  | 6513 | RS-485 Comm Port (M/S) Number Of Exceptions | 1 | INT16U | R | Y | --- | Number of exception replies
Inputs & Outputs
Demand Sync Setup
Digital Input Associations With Demand Systems
|  |  | 7020 | Demand System 1 (Power) | 1 | INT16U | RWC | Y | ---
|  |  | 7021 | Demand System 2 (Current) | 1 | INT16U | RWC | Y | ---
Digital Output Associations With Demand Systems
|  |  | 7026 | Demand System 1 (Power) | 1 | INT16U | RWC | Y | ---
|  |  | 7027 | Demand System 2 (Current) | 1 | INT16U | RWC | Y | ---
Digital Inputs Setup
Base Unit - Digital Input DI1
|  |  | 7273 | Type | 1 | INT16U | R | N | --- | First digit (1) indicates point is digital input Second digit indicates the digital input module type Second digit can be used to identify specific hardware options. 0 = Generic digital input Third digit indicates input type 1 = AC 2 = DC
|  |  | 7274 | Control Mode | 1 | INT16U | RWC | N | --- | 0 = Normal (Alarm) 1 = Demand Interval Sync Pulse 2 = Multi-tariff Control 3 = Input Metering 4 = Conditional Energy Control 5 = Incremental Energy Reset
|  |  | 7275 | Label | 20 | UTF8 | RWC | Y | ---
|  |  | 7295 | Debounce Time | 1 | INT16U | RWC | Y | msec | Must be entered in increments of 10ms.
Base Unit - Digital Input DI2
|  |  | 7297 | Type | 1 | INT16U | R | N | ---
|  |  | 7298 | Control Mode | 1 | INT16U | RWC | N | ---
|  |  | 7299 | Label | 20 | UTF8 | RWC | Y | ---
|  |  | 7319 | Debounce Time | 1 | INT16U | RWC | Y | msec | Must be entered in increments of 10ms.
Base Unit - Digital Input DI3
|  |  | 7321 | Type | 1 | INT16U | R | N | ---
|  |  | 7322 | Control Mode | 1 | INT16U | RWC | N | ---
|  |  | 7323 | Label | 20 | UTF8 | RWC | Y | ---
|  |  | 7343 | Debounce Time | 1 | INT16U | RWC | Y | msec | Must be entered in increments of 10ms.
Base Unit - Digital Input DI4
|  |  | 7345 | Type | 1 | INT16U | R | N | ---
|  |  | 7346 | Control Mode | 1 | INT16U | RWC | N | ---
|  |  | 7347 | Label | 20 | UTF8 | RWC | Y | ---
|  |  | 7367 | Debounce Time | 1 | INT16U | RWC | Y | msec | Must be entered in increments of 10ms.
Digital Inputs Status
On/Off Status
|  |  | 8905 | Digital Input Status – Base Unit | 2 | BITMAP | R | N | ---
Base Unit - Digital Input DI1
|  |  | 8915 | Count | 2 | INT32U | R | Y | ---
|  |  | 8917 | On Time | 2 | INT32U | R | Y | seconds
Base Unit - Digital Input DI2
|  |  | 8919 | Count | 2 | INT32U | R | Y | ---
|  |  | 8921 | On Time | 2 | INT32U | R | Y | seconds
Base Unit - Digital Input DI3
|  |  | 8923 | Count | 2 | INT32U | R | Y | ---
|  |  | 8925 | On Time | 2 | INT32U | R | Y | seconds
Base Unit - Digital Input DI4
|  |  | 8927 | Count | 2 | INT32U | R | Y | ---
|  |  | 8929 | On Time | 2 | INT32U | R | Y | seconds
Digital Outputs Setup
Base Unit - Digital Output DO1
|  |  | 9187 | Type | 1 | INT16U | R | N | --- | First digit (2) indicates point is digital output Second digit indicates module type 0 = Generic Digital output Third digit indicates output type 1 = solid state relay 2 = electromechanical relay
|  |  | 9188 | Label | 20 | UTF8 | RWC | Y | ---
|  |  | 9209 | Behavioral Mode | 1 | INT16U | RWC | Y | --- | 0 = Normal (forced by a control mode of Energy) 1 = Timed (forced by a control mode of Demand Sync) 2 = Coil Hold
|  |  | 9210 | On Time For Timed Mode | 1 | INT16U | RWC | Y | seconds | The time for the output to remain energized when the output is energized in timed mode.
Base Unit - Digital Output DO2
|  |  | 9211 | Type | 1 | INT16U | R | N | ---
|  |  | 9212 | Label | 20 | UTF8 | RWC | Y | ---
|  |  | 9233 | Behavioral Mode | 1 | INT16U | RWC | Y | --- | 0 = Normal 1 = Timed 2 = Coil Hold
|  |  | 9234 | On Time For Timed Mode | 1 | INT16U | RWC | Y | seconds | The time for the output to remain energized when the output is energized in timed mode.
Digital Outputs Status
On/Off Status
|  |  | 9667 | Digital Output Status – Base Unit | 1 | BITMAP | R | Y | ---
Base Unit - Digital Output DO1
|  |  | 9672 | Operating Mode Status | 1 | INT16U | R | N | --- | 0 = Normal, 1 = Override Operating Mode is changed by command. Override is considered a temporary condition used for troubleshooting. The state is volatile. That is to say that if the meter resets, the digital output will revert to normal operation.
|  |  | 9673 | Control Mode Status | 1 | INT16U | R | N | --- | 0 = External 1 = Demand Sync 2 = Alarm 3 = Energy (Energy control modes are not available for electromechanical relays.)
|  |  | 9674 | Behavioral Mode Status | 1 | INT16U | R | Y | --- | 0 = Normal 1 = Timed 2 = Coil Hold (Behavioral Mode will be forced to Normal when in Override Operating Mode.)
|  |  | 9675 | Count | 2 | INT32U | R | Y | ---
|  |  | 9677 | On Time | 2 | INT32U | R | Y | seconds
Base Unit - Digital Output DO2
|  |  | 9680 | Operating Mode Status | 1 | INT16U | R | N | ---
|  |  | 9681 | Control Mode Status | 1 | INT16U | R | N | ---
|  |  | 9682 | Behavioral Mode Status | 1 | INT16U | R | Y | ---
|  |  | 9683 | Count | 2 | INT32U | R | Y | ---
|  |  | 9685 | On Time | 2 | INT32U | R | Y | seconds
Alarms
Alarm Status
Detected Priority Status
|  |  | 11010 | Detected Priority Status Bitmap | 1 | BITMAP | R | N | --- | Bit 01 = 1 if any priority 1-3 alarm is active Bit 02 = 1 if a “High” (1) priority alarm is active Bit 03 = 1 if a “Medium” (2) priority alarm is active Bit 04 = 1 if a “Low” (3) priority alarm is active Bit 05 = 1 if a "None" (0) priority alarm is active
Enabled Alarm Bitmaps
|  |  | 11040 | Standard – 1 second 1 | 1 | BITMAP | R | N | --- | 0 = Disabled; 1 = Enabled
|  |  | 11041 | Standard – 1 second 2 | 1 | BITMAP | R | N | ---
|  |  | 11042 | Standard – 1 second 3 | 1 | BITMAP | R | N | ---
|  |  | 11050 | Unary | 1 | BITMAP | R | N | ---
|  |  | 11051 | Digital 1 | 1 | BITMAP | R | N | ---
Detected Alarm Bitmaps
|  |  | 11059 | Standard – 1 second Group 1 | 1 | BITMAP | R | N | --- | 0 = Not Detected; 1 = Detected
|  |  | 11060 | Standard – 1 second Group 2 | 1 | BITMAP | R | N | ---
|  |  | 11061 | Standard – 1 second Group 3 | 1 | BITMAP | R | N | ---
|  |  | 11069 | Unary | 1 | BITMAP | R | N | ---
|  |  | 11070 | Digital Group 1 | 1 | BITMAP | R | N | ---
Unacknowledged High Priority Alarm Bitmaps
|  |  | 11078 | Standard – 1 second 1 | 1 | BITMAP | R | N | --- | 0 = Acknowledged; 1 = Unacknowledged
|  |  | 11079 | Standard – 1 second 2 | 1 | BITMAP | R | N | ---
|  |  | 11080 | Standard – 1 second 3 | 1 | BITMAP | R | N | ---
|  |  | 11088 | Unary | 1 | BITMAP | R | N | ---
|  |  | 11089 | Digital 1 | 1 | BITMAP | R | N | ---
Alarm Event Queue
|  |  | 11111 | Version of Event Queue | 1 | INT16U | R | N | ---
|  |  | 11113 | Size of Event Queue | 1 | INT16U | R | N | ---
|  |  | 11114 | Number of Entries in Event Queue | 1 | INT16U | R | Y | ---
|  |  | 11115 | Entry Number of Most Recent Event | 1 | INT16U | R | Y | --- | Rolls over from 65535 to 0.
Entry 001
|  |  | 11116 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11117 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11121 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11122 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11123 | Value | 4 | INT16U | R | N | ---
|  |  | 11127 | Sequence Number | 1 | INT16U | R | N | ---
Entry 002
|  |  | 11128 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11129 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11133 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11134 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11135 | Value | 4 | INT16U | R | N | ---
|  |  | 11139 | Sequence Number | 1 | INT16U | R | N | ---
Entry 003
|  |  | 11140 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11141 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11145 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11146 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11147 | Value | 4 | INT16U | R | N | ---
|  |  | 11151 | Sequence Number | 1 | INT16U | R | N | ---
Entry 004
|  |  | 11152 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11153 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11157 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11158 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11159 | Value | 4 | INT16U | R | N | ---
|  |  | 11163 | Sequence Number | 1 | INT16U | R | N | ---
Entry 005
|  |  | 11164 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11165 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11169 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11170 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11171 | Value | 4 | INT16U | R | N | ---
|  |  | 11175 | Sequence Number | 1 | INT16U | R | N | ---
Entry 006
|  |  | 11176 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11177 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11181 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11182 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11183 | Value | 4 | INT16U | R | N | ---
|  |  | 11187 | Sequence Number | 1 | INT16U | R | N | ---
Entry 007
|  |  | 11188 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11189 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11193 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11194 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11195 | Value | 4 | INT16U | R | N | ---
|  |  | 11199 | Sequence Number | 1 | INT16U | R | N | ---
Entry 008
|  |  | 11200 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11201 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11205 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11206 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11207 | Value | 4 | INT16U | R | N | ---
|  |  | 11211 | Sequence Number | 1 | INT16U | R | N | ---
Entry 009
|  |  | 11212 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11213 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11217 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11218 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11219 | Value | 4 | INT16U | R | N | ---
|  |  | 11223 | Sequence Number | 1 | INT16U | R | N | ---
Entry 010
|  |  | 11224 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11225 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11229 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11230 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11231 | Value | 4 | INT16U | R | N | ---
|  |  | 11235 | Sequence Number | 1 | INT16U | R | N | ---
Entry 011
|  |  | 11236 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11237 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11241 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11242 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11243 | Value | 4 | INT16U | R | N | ---
|  |  | 11247 | Sequence Number | 1 | INT16U | R | N | ---
Entry 012
|  |  | 11248 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11249 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11253 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11254 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11255 | Value | 4 | INT16U | R | N | ---
|  |  | 11259 | Sequence Number | 1 | INT16U | R | N | ---
Entry 013
|  |  | 11260 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11261 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11265 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11266 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11267 | Value | 4 | INT16U | R | N | ---
|  |  | 11271 | Sequence Number | 1 | INT16U | R | N | ---
Entry 014
|  |  | 11272 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11273 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11277 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11278 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11279 | Value | 4 | INT16U | R | N | ---
|  |  | 11283 | Sequence Number | 1 | INT16U | R | N | ---
Entry 015
|  |  | 11284 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11285 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11289 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11290 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11291 | Value | 4 | INT16U | R | N | ---
|  |  | 11295 | Sequence Number | 1 | INT16U | R | N | ---
Entry 016
|  |  | 11296 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11297 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11301 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11302 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11303 | Value | 4 | INT16U | R | N | ---
|  |  | 11307 | Sequence Number | 1 | INT16U | R | N | ---
Entry 017
|  |  | 11308 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11309 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11313 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11314 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11315 | Value | 4 | INT16U | R | N | ---
|  |  | 11319 | Sequence Number | 1 | INT16U | R | N | ---
Entry 018
|  |  | 11320 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11321 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11325 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11326 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11327 | Value | 4 | INT16U | R | N | ---
|  |  | 11331 | Sequence Number | 1 | INT16U | R | N | ---
Entry 019
|  |  | 11332 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11333 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11337 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11338 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11339 | Value | 4 | INT16U | R | N | ---
|  |  | 11343 | Sequence Number | 1 | INT16U | R | N | ---
Entry 020
|  |  | 11344 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11345 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11349 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11350 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11351 | Value | 4 | INT16U | R | N | ---
|  |  | 11355 | Sequence Number | 1 | INT16U | R | N | ---
Entry 021
|  |  | 11356 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11357 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11361 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11362 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11363 | Value | 4 | INT16U | R | N | ---
|  |  | 11367 | Sequence Number | 1 | INT16U | R | N | ---
Entry 022
|  |  | 11368 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11369 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11373 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11374 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11375 | Value | 4 | INT16U | R | N | ---
|  |  | 11379 | Sequence Number | 1 | INT16U | R | N | ---
Entry 023
|  |  | 11380 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11381 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11385 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11386 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11387 | Value | 4 | INT16U | R | N | ---
|  |  | 11391 | Sequence Number | 1 | INT16U | R | N | ---
Entry 024
|  |  | 11392 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11393 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11397 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11398 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11399 | Value | 4 | INT16U | R | N | ---
|  |  | 11403 | Sequence Number | 1 | INT16U | R | N | ---
Entry 025
|  |  | 11404 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11405 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11409 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11410 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11411 | Value | 4 | INT16U | R | N | ---
|  |  | 11415 | Sequence Number | 1 | INT16U | R | N | ---
Entry 026
|  |  | 11416 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11417 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11421 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11422 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11423 | Value | 4 | INT16U | R | N | ---
|  |  | 11427 | Sequence Number | 1 | INT16U | R | N | ---
Entry 027
|  |  | 11428 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11429 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11433 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11434 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11435 | Value | 4 | INT16U | R | N | ---
|  |  | 11439 | Sequence Number | 1 | INT16U | R | N | ---
Entry 028
|  |  | 11440 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11441 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11445 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11446 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11447 | Value | 4 | INT16U | R | N | ---
|  |  | 11451 | Sequence Number | 1 | INT16U | R | N | ---
Entry 029
|  |  | 11452 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11453 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11457 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11458 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11459 | Value | 4 | INT16U | R | N | ---
|  |  | 11463 | Sequence Number | 1 | INT16U | R | N | ---
Entry 030
|  |  | 11464 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11465 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11469 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11470 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11471 | Value | 4 | INT16U | R | N | ---
|  |  | 11475 | Sequence Number | 1 | INT16U | R | N | ---
Entry 031
|  |  | 11476 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11477 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11481 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11482 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11483 | Value | 4 | INT16U | R | N | ---
|  |  | 11487 | Sequence Number | 1 | INT16U | R | N | ---
Entry 032
|  |  | 11488 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11489 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11493 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11494 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11495 | Value | 4 | INT16U | R | N | ---
|  |  | 11499 | Sequence Number | 1 | INT16U | R | N | ---
Entry 033
|  |  | 11500 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11501 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11505 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11506 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11507 | Value | 4 | INT16U | R | N | ---
|  |  | 11511 | Sequence Number | 1 | INT16U | R | N | ---
Entry 034
|  |  | 11512 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11513 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11517 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11518 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11519 | Value | 4 | INT16U | R | N | ---
|  |  | 11523 | Sequence Number | 1 | INT16U | R | N | ---
Entry 035
|  |  | 11524 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11525 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11529 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11530 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11531 | Value | 4 | INT16U | R | N | ---
|  |  | 11535 | Sequence Number | 1 | INT16U | R | N | ---
Entry 036
|  |  | 11536 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11537 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11541 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11542 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11543 | Value | 4 | INT16U | R | N | ---
|  |  | 11547 | Sequence Number | 1 | INT16U | R | N | ---
Entry 037
|  |  | 11548 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11549 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11553 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11554 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11555 | Value | 4 | INT16U | R | N | ---
|  |  | 11559 | Sequence Number | 1 | INT16U | R | N | ---
Entry 038
|  |  | 11560 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11561 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11565 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11566 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11567 | Value | 4 | INT16U | R | N | ---
|  |  | 11571 | Sequence Number | 1 | INT16U | R | N | ---
Entry 039
|  |  | 11572 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11573 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11577 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11578 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11579 | Value | 4 | INT16U | R | N | ---
|  |  | 11583 | Sequence Number | 1 | INT16U | R | N | ---
Entry 040
|  |  | 11584 | Entry Number | 1 | INT16U | R | N | ---
|  |  | 11585 | Date/Time | 4 | DATETIME | R | N | ---
|  |  | 11589 | Record Type | 1 | INT16U | R | N | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 11590 | Register Number or Event Code | 1 | INT16U | R | N | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 11591 | Value | 4 | INT16U | R | N | ---
|  |  | 11595 | Sequence Number | 1 | INT16U | R | N | ---
Alarm History Log
|  |  | 12316 | Size of History Log | 1 | INT16U | R | N | ---
|  |  | 12317 | Number of Entries in History Log | 1 | INT16U | R | Y | ---
|  |  | 12318 | Entry Number of Most Recent Event | 1 | INT16U | R | Y | --- | Value rolls over from 65535 (0xFFFF) to 0.
Entry 001
|  |  | 12319 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12320 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12324 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12325 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12326 | Value | 4 | INT16U | R | Y | ---
|  |  | 12330 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 002
|  |  | 12331 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12332 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12336 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12337 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12338 | Value | 4 | INT16U | R | Y | ---
|  |  | 12342 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 003
|  |  | 12343 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12344 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12348 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12349 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12350 | Value | 4 | INT16U | R | Y | ---
|  |  | 12354 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 004
|  |  | 12355 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12356 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12360 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12361 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12362 | Value | 4 | INT16U | R | Y | ---
|  |  | 12366 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 005
|  |  | 12367 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12368 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12372 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12373 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12374 | Value | 4 | INT16U | R | Y | ---
|  |  | 12378 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 006
|  |  | 12379 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12380 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12384 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12385 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12386 | Value | 4 | INT16U | R | Y | ---
|  |  | 12390 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 007
|  |  | 12391 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12392 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12396 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12397 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12398 | Value | 4 | INT16U | R | Y | ---
|  |  | 12402 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 008
|  |  | 12403 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12404 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12408 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12409 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12410 | Value | 4 | INT16U | R | Y | ---
|  |  | 12414 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 009
|  |  | 12415 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12416 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12420 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12421 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12422 | Value | 4 | INT16U | R | Y | ---
|  |  | 12426 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 010
|  |  | 12427 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12428 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12432 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12433 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12434 | Value | 4 | INT16U | R | Y | ---
|  |  | 12438 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 011
|  |  | 12439 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12440 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12444 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12445 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12446 | Value | 4 | INT16U | R | Y | ---
|  |  | 12450 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 012
|  |  | 12451 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12452 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12456 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12457 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12458 | Value | 4 | INT16U | R | Y | ---
|  |  | 12462 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 013
|  |  | 12463 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12464 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12468 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12469 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12470 | Value | 4 | INT16U | R | Y | ---
|  |  | 12474 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 014
|  |  | 12475 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12476 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12480 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12481 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12482 | Value | 4 | INT16U | R | Y | ---
|  |  | 12486 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 015
|  |  | 12487 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12488 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12492 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12493 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12494 | Value | 4 | INT16U | R | Y | ---
|  |  | 12498 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 016
|  |  | 12499 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12500 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12504 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12505 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12506 | Value | 4 | INT16U | R | Y | ---
|  |  | 12510 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 017
|  |  | 12511 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12512 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12516 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12517 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12518 | Value | 4 | INT16U | R | Y | ---
|  |  | 12522 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 018
|  |  | 12523 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12524 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12528 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12529 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12530 | Value | 4 | INT16U | R | Y | ---
|  |  | 12534 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 019
|  |  | 12535 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12536 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12540 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12541 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12542 | Value | 4 | INT16U | R | Y | ---
|  |  | 12546 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 020
|  |  | 12547 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12548 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12552 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12553 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12554 | Value | 4 | INT16U | R | Y | ---
|  |  | 12558 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 021
|  |  | 12559 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12560 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12564 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12565 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12566 | Value | 4 | INT16U | R | Y | ---
|  |  | 12570 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 022
|  |  | 12571 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12572 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12576 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12577 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12578 | Value | 4 | INT16U | R | Y | ---
|  |  | 12582 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 023
|  |  | 12583 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12584 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12588 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12589 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12590 | Value | 4 | INT16U | R | Y | ---
|  |  | 12594 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 024
|  |  | 12595 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12596 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12600 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12601 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12602 | Value | 4 | INT16U | R | Y | ---
|  |  | 12606 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 025
|  |  | 12607 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12608 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12612 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12613 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12614 | Value | 4 | INT16U | R | Y | ---
|  |  | 12618 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 026
|  |  | 12619 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12620 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12624 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12625 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12626 | Value | 4 | INT16U | R | Y | ---
|  |  | 12630 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 027
|  |  | 12631 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12632 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12636 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12637 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12638 | Value | 4 | INT16U | R | Y | ---
|  |  | 12642 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 028
|  |  | 12643 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12644 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12648 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12649 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12650 | Value | 4 | INT16U | R | Y | ---
|  |  | 12654 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 029
|  |  | 12655 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12656 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12660 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12661 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12662 | Value | 4 | INT16U | R | Y | ---
|  |  | 12666 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 030
|  |  | 12667 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12668 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12672 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12673 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12674 | Value | 4 | INT16U | R | Y | ---
|  |  | 12678 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 031
|  |  | 12679 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12680 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12684 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12685 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12686 | Value | 4 | INT16U | R | Y | ---
|  |  | 12690 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 032
|  |  | 12691 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12692 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12696 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12697 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12698 | Value | 4 | INT16U | R | Y | ---
|  |  | 12702 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 033
|  |  | 12703 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12704 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12708 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12709 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12710 | Value | 4 | INT16U | R | Y | ---
|  |  | 12714 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 034
|  |  | 12715 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12716 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12720 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12721 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12722 | Value | 4 | INT16U | R | Y | ---
|  |  | 12726 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 035
|  |  | 12727 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12728 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12732 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12733 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12734 | Value | 4 | INT16U | R | Y | ---
|  |  | 12738 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 036
|  |  | 12739 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12740 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12744 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12745 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12746 | Value | 4 | INT16U | R | Y | ---
|  |  | 12750 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 037
|  |  | 12751 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12752 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12756 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12757 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12758 | Value | 4 | INT16U | R | Y | ---
|  |  | 12762 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 038
|  |  | 12763 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12764 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12768 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12769 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12770 | Value | 4 | INT16U | R | Y | ---
|  |  | 12774 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 039
|  |  | 12775 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12776 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12780 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12781 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12782 | Value | 4 | INT16U | R | Y | ---
|  |  | 12786 | Sequence Number | 1 | INT16U | R | Y | ---
Entry 040
|  |  | 12787 | Entry Number | 1 | INT16U | R | Y | ---
|  |  | 12788 | Date/Time | 4 | DATETIME | R | Y | ---
|  |  | 12792 | Record Type | 1 | INT16U | R | Y | --- | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | 12793 | Register Number or Event Code | 1 | INT16U | R | Y | --- | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | 12794 | Value | 4 | INT16U | R | Y | ---
|  |  | 12798 | Sequence Number | 1 | INT16U | R | Y | ---
Alarm Counters
Summary
|  |  | 13519 | Total Counter | 1 | INT16U | R | Y | ---
|  |  | 13520 | Low Priority Counter | 1 | INT16U | R | Y | ---
|  |  | 13521 | Medium Priority Counter | 1 | INT16U | R | Y | ---
|  |  | 13522 | High Priority Counter | 1 | INT16U | R | Y | ---
1-Second Alarms - Standard
|  |  | 13523 | Over Current, Phase | 1 | INT16U | R | Y | ---
|  |  | 13524 | Under Current, Phase | 1 | INT16U | R | Y | ---
|  |  | 13525 | Over Current, Neutral | 1 | INT16U | R | Y | ---
|  |  | 13526 | Over Current, Ground | 1 | INT16U | R | Y | ---
|  |  | 13527 | Over Voltage, L-L | 1 | INT16U | R | Y | ---
|  |  | 13528 | Under Voltage, L-L | 1 | INT16U | R | Y | ---
|  |  | 13529 | Over Voltage, L-N | 1 | INT16U | R | Y | ---
|  |  | 13530 | Under Voltage, L-N | 1 | INT16U | R | Y | ---
|  |  | 13531 | Over Power, Active | 1 | INT16U | R | Y | ---
|  |  | 13532 | Over Power, Reactive | 1 | INT16U | R | Y | ---
|  |  | 13533 | Over Power, Apparent | 1 | INT16U | R | Y | ---
|  |  | 13534 | Lead Power Factor, True | 1 | INT16U | R | Y | ---
|  |  | 13535 | Lag Power Factor, True | 1 | INT16U | R | Y | ---
|  |  | 13536 | Lead Power Factor, Displacement | 1 | INT16U | R | Y | ---
|  |  | 13537 | Lag Power Factor, Displacement | 1 | INT16U | R | Y | ---
|  |  | 13538 | Over Demand, Active Power, Present | 1 | INT16U | R | Y | ---
|  |  | 13539 | Over Demand, Active Power, Last | 1 | INT16U | R | Y | ---
|  |  | 13540 | Over Demand, Active Power, Predicted | 1 | INT16U | R | Y | ---
|  |  | 13541 | Over Demand, Reactive Power, Present | 1 | INT16U | R | Y | ---
|  |  | 13542 | Over Demand, Reactive Power, Last | 1 | INT16U | R | Y | ---
|  |  | 13543 | Over Demand, Reactive Power, Predicted | 1 | INT16U | R | Y | ---
|  |  | 13544 | Over Demand, Apparent Power, Present | 1 | INT16U | R | Y | ---
|  |  | 13545 | Over Demand, Apparent Power, Last | 1 | INT16U | R | Y | ---
|  |  | 13546 | Over Demand, Apparent Power, Predicted | 1 | INT16U | R | Y | ---
|  |  | 13547 | Over Frequency | 1 | INT16U | R | Y | ---
|  |  | 13548 | Under Frequency | 1 | INT16U | R | Y | ---
|  |  | 13549 | Over Voltage Unbalance | 1 | INT16U | R | Y | ---
|  |  | 13550 | Over Voltage Total Harmonic Distortion | 1 | INT16U | R | Y | ---
|  |  | 13551 | Phase Loss | 1 | INT16U | R | Y | ---
Unary Alarms
|  |  | 13623 | Meter Powerup (Control Power Loss) | 1 | INT16U | R | Y | ---
|  |  | 13624 | Meter Reset | 1 | INT16U | R | Y | ---
|  |  | 13625 | Meter Diagnostic | 1 | INT16U | R | Y | ---
|  |  | 13626 | Phase Reversal | 1 | INT16U | R | Y | ---
Digital Alarms
|  |  | 13633 | Digital Alarm DI1 | 1 | INT16U | R | Y | ---
|  |  | 13634 | Digital Alarm DI2 | 1 | INT16U | R | Y | ---
|  |  | 13635 | Digital Alarm DI3 | 1 | INT16U | R | Y | ---
|  |  | 13636 | Digital Alarm DI4 | 1 | INT16U | R | Y | ---
1-Second Alarms - Standard
Over Current, Phase
|  |  | 14000 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14002 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14003 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14004 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14005 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | A | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | 14007 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14009 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | A | Must be < Pickup Setpoint.
|  |  | 14011 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14013 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Under Current, Phase
|  |  | 14020 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14022 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14023 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14024 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14025 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | A | Must be < Dropout Setpoint.
|  |  | 14027 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14029 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | A | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | 14031 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14033 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Current, Neutral
|  |  | 14040 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14042 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14043 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14044 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14045 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | A | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | 14047 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14049 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | A | Must be < Pickup Setpoint.
|  |  | 14051 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14053 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Current, Ground
|  |  | 14060 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14062 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14063 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14064 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14065 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | A | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | 14067 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14069 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | A | Must be < Pickup Setpoint.
|  |  | 14071 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14073 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Voltage, L-L
|  |  | 14080 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14082 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14083 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14084 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14085 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | V | The maximum pickup setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | 14087 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14089 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | V | Must be < Pickup Setpoint.
|  |  | 14091 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14093 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Under Voltage, L-L
|  |  | 14100 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14102 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14103 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14104 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14105 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | V | Must be < Dropout Setpoint.
|  |  | 14107 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14109 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | V | The maximum dropout setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | 14111 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14113 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Voltage, L-N
|  |  | 14120 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14122 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14123 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14124 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14125 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | V | The maximum pickup setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | 14127 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14129 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | V | Must be < Pickup Setpoint.
|  |  | 14131 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14133 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Under Voltage, L-N
|  |  | 14140 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14142 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14143 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14144 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14145 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | V | Must be < Dropout Setpoint.
|  |  | 14147 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14149 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | V | The maximum dropout setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | 14151 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14153 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Power, Active
|  |  | 14160 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14162 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14163 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14164 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14165 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kW | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14167 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14169 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kW | Must be < Pickup Setpoint.
|  |  | 14171 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14173 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Power, Reactive
|  |  | 14180 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14182 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14183 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14184 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14185 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kVAR | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14187 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14189 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kVAR | Must be < Pickup Setpoint.
|  |  | 14191 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14193 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Power, Apparent
|  |  | 14200 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14202 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14203 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14204 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14205 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kVA | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14207 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14209 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kVA | Must be < Pickup Setpoint.
|  |  | 14211 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14213 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Leading Power Factor, True
|  |  | 14220 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14222 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14223 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14224 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14225 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | ---
|  |  | 14227 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14229 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | ---
|  |  | 14231 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14233 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Lagging Power Factor, True
|  |  | 14240 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14242 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14243 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14244 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14245 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | ---
|  |  | 14247 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14249 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | ---
|  |  | 14251 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14253 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Leading Power Factor, Displacement
|  |  | 14260 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14262 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14263 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14264 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14265 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | ---
|  |  | 14267 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14269 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | ---
|  |  | 14271 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14273 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Lagging Power Factor, Displacement
|  |  | 14280 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14282 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14283 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14284 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14285 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | ---
|  |  | 14287 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14289 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | ---
|  |  | 14291 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14293 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Demand, Active Power, Present
|  |  | 14300 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14302 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14303 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14304 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14305 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kW | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14307 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14309 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kW | Must be < Pickup Setpoint.
|  |  | 14311 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14313 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Demand, Active Power, Last
|  |  | 14320 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14322 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14323 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14324 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14325 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kW | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14327 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14329 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kW | Must be < Pickup Setpoint.
|  |  | 14331 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14333 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Demand, Active Power, Predicted
|  |  | 14340 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14342 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14343 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14344 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14345 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kW | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14347 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14349 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kW | Must be < Pickup Setpoint.
|  |  | 14351 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14353 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Demand, Reactive Power, Present
|  |  | 14360 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14362 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14363 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14364 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14365 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kVAR | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14367 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14369 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kVAR | Must be < Pickup Setpoint.
|  |  | 14371 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14373 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Demand, Reactive Power, Last
|  |  | 14380 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14382 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14383 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14384 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14385 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kVAR | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14387 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14389 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kVAR | Must be < Pickup Setpoint.
|  |  | 14391 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14393 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Demand, Reactive Power, Predicted
|  |  | 14400 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14402 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14403 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14404 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14405 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kVAR | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14407 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14409 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kVAR | Must be < Pickup Setpoint.
|  |  | 14411 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14413 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Demand, Apparent Power, Present
|  |  | 14420 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14422 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14423 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14424 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14425 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kVA | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14427 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14429 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kVA | Must be < Pickup Setpoint.
|  |  | 14431 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14433 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Demand, Apparent Power, Last
|  |  | 14440 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14442 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14443 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14444 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14445 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kVA | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14447 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14449 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kVA | Must be < Pickup Setpoint.
|  |  | 14451 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14453 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Demand, Apparent Power, Predicted
|  |  | 14460 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14462 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14463 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14464 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14465 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | kVA | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | 14467 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14469 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | kVA | Must be < Pickup Setpoint.
|  |  | 14471 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14473 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Frequency
|  |  | 14480 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14482 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14483 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14484 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14485 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | Hz
|  |  | 14487 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14489 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | Hz | Must be < Pickup Setpoint.
|  |  | 14491 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14493 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Under Frequency
|  |  | 14500 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14502 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14503 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14504 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14505 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | Hz | Must be < Dropout Setpoint.
|  |  | 14507 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14509 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | Hz
|  |  | 14511 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14513 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Voltage Unbalance
|  |  | 14520 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14522 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14523 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14524 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14525 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | %
|  |  | 14527 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14529 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | % | Must be < Pickup Setpoint.
|  |  | 14531 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14533 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Over Voltage Total Harmonic Distortion
|  |  | 14540 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14542 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14543 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14544 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14545 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | %
|  |  | 14547 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14549 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | % | Must be < Pickup Setpoint.
|  |  | 14551 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14553 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Phase Loss
|  |  | 14560 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 14562 | Source Register A | 1 | INT16U | R | N | ---
|  |  | 14563 | Source Register B | 1 | INT16U | R | N | ---
|  |  | 14564 | Source Register C | 1 | INT16U | R | N | ---
|  |  | 14565 | Pickup Setpoint | 2 | FLOAT32 | RWC | Y | V | Must be < Dropout Setpoint.
|  |  | 14567 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14569 | Dropout Setpoint | 2 | FLOAT32 | RWC | Y | V
|  |  | 14571 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 14573 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Meter Power Up (Control Power Loss)
|  |  | 16200 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 16202 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Meter Reset
|  |  | 16210 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 16212 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Meter Diagnostic
|  |  | 16220 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 16222 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Phase Reversal
|  |  | 16230 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 16232 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Digital Alarms
Digital Alarm DI1
|  |  | 16300 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 16302 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 16304 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 16306 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Digital Alarm DI2
|  |  | 16314 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 16316 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 16318 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 16320 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Digital Alarm DI3
|  |  | 16328 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 16330 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 16332 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 16334 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Digital Alarm DI4
|  |  | 16342 | Attributes | 2 | INT32U | RWC | Y | --- | See Alarm Attributes for details.
|  |  | 16344 | Pickup Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 16346 | Dropout Time Delay | 2 | INT32U | RWC | Y | seconds
|  |  | 16348 | Digital Outputs to Associate – Standard | 1 | BITMAP | RWC | Y | --- | Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Diagnostics
Self-Test Results
Miscellaneous Self-Test
|  |  | 20003 | Meter Self-Test | 5 | BITMAP | R | N | --- | 0 = OK, 1 = Error Detected Bit 01 = Summary ( on if any other bit is on - Maintenance Icon shown on HMI ) Bit 02 = RAM Failure Bit 03 = NVRAM Failure Bit 04 = RTC Failure Bit 05 = Calibration Failure Bit 06 = Clipping Detected Bit 07 = Over-Running Energy Pulse Output Bit 08-16 Not Used
Meter Data (Advanced)
Frequency
|  |  | 21016 | Frequency 1 Cycle | 2 | FLOAT32 | R | N | Hz
Power Quality
Total Harmonic Distortion, Current
|  |  | 21300 | THD Current A | 2 | FLOAT32 | R | N | % | THD = (RMS of harmonics / RMS of fundamental) * 100
|  |  | 21302 | THD Current B | 2 | FLOAT32 | R | N | %
|  |  | 21304 | THD Current C | 2 | FLOAT32 | R | N | %
|  |  | 21306 | THD Current N | 2 | FLOAT32 | R | N | %
|  |  | 21308 | THD Current G | 2 | FLOAT32 | R | N | %
|  |  | 21310 | thd Current A | 2 | FLOAT32 | R | N | % | thd = (RMS of harmonics / total RMS) * 100
|  |  | 21312 | thd Current B | 2 | FLOAT32 | R | N | %
|  |  | 21314 | thd Current C | 2 | FLOAT32 | R | N | %
|  |  | 21316 | thd Current N | 2 | FLOAT32 | R | N | %
|  |  | 21318 | thd Current G | 2 | FLOAT32 | R | N | %
Total Demand Distortion
|  |  | 21320 | Total Demand Distortion | 2 | FLOAT32 | R | N | %
Total Harmonic Distortion, Voltage
|  |  | 21322 | THD Voltage A-B | 2 | FLOAT32 | R | N | %
|  |  | 21324 | THD Voltage B-C | 2 | FLOAT32 | R | N | %
|  |  | 21326 | THD Voltage C-A | 2 | FLOAT32 | R | N | %
|  |  | 21328 | THD Voltage L-L | 2 | FLOAT32 | R | N | %
|  |  | 21330 | THD Voltage A-N | 2 | FLOAT32 | R | N | %
|  |  | 21332 | THD Voltage B-N | 2 | FLOAT32 | R | N | %
|  |  | 21334 | THD Voltage C-N | 2 | FLOAT32 | R | N | %
|  |  | 21338 | THD Voltage L-N | 2 | FLOAT32 | R | N | %
|  |  | 21340 | thd Voltage A-B | 2 | FLOAT32 | R | N | %
|  |  | 21342 | thd Voltage B-C | 2 | FLOAT32 | R | N | %
|  |  | 21344 | thd Voltage C-A | 2 | FLOAT32 | R | N | %
|  |  | 21346 | thd Voltage L-L | 2 | FLOAT32 | R | N | %
|  |  | 21348 | thd Voltage A-N | 2 | FLOAT32 | R | N | %
|  |  | 21350 | thd Voltage B-N | 2 | FLOAT32 | R | N | %
|  |  | 21352 | thd Voltage C-N | 2 | FLOAT32 | R | N | %
|  |  | 21356 | thd Voltage L-N | 2 | FLOAT32 | R | N | %
Minimum Values
|  |  | 27214 | Min/Max Reset Datetime | 4 | DATETIME | R | Y | ---
Current
|  |  | 27218 | Min Current A | 2 | FLOAT32 | R | Y | A
|  |  | 27220 | Min Current B | 2 | FLOAT32 | R | Y | A
|  |  | 27222 | Min Current C | 2 | FLOAT32 | R | Y | A
|  |  | 27224 | Min Current N | 2 | FLOAT32 | R | Y | A
|  |  | 27226 | Min Current G | 2 | FLOAT32 | R | Y | A
|  |  | 27228 | Min Current Avg | 2 | FLOAT32 | R | Y | A
Current Unbalance
|  |  | 27230 | Min Current Unbalance A | 2 | FLOAT32 | R | Y | %
|  |  | 27232 | Min Current Unbalance B | 2 | FLOAT32 | R | Y | %
|  |  | 27234 | Min Current Unbalance C | 2 | FLOAT32 | R | Y | %
|  |  | 27236 | Min Current Unbalance Worst | 2 | FLOAT32 | R | Y | %
Voltage
|  |  | 27238 | Min Voltage A-B | 2 | FLOAT32 | R | Y | V
|  |  | 27240 | Min Voltage B-C | 2 | FLOAT32 | R | Y | V
|  |  | 27242 | Min Voltage C-A | 2 | FLOAT32 | R | Y | V
|  |  | 27244 | Min Voltage L-L Avg | 2 | FLOAT32 | R | Y | V
|  |  | 27246 | Min Voltage A-N | 2 | FLOAT32 | R | Y | V
|  |  | 27248 | Min Voltage B-N | 2 | FLOAT32 | R | Y | V
|  |  | 27250 | Min Voltage C-N | 2 | FLOAT32 | R | Y | V
|  |  | 27254 | Min Voltage L-N Avg | 2 | FLOAT32 | R | Y | V
Voltage Unbalance
|  |  | 27256 | Min Voltage Unbalance A-B | 2 | FLOAT32 | R | Y | %
|  |  | 27258 | Min Voltage Unbalance B-C | 2 | FLOAT32 | R | Y | %
|  |  | 27260 | Min Voltage Unbalance C-A | 2 | FLOAT32 | R | Y | %
|  |  | 27262 | Min Voltage Unbalance L-L Worst | 2 | FLOAT32 | R | Y | %
|  |  | 27264 | Min Voltage Unbalance A-N | 2 | FLOAT32 | R | Y | %
|  |  | 27266 | Min Voltage Unbalance B-N | 2 | FLOAT32 | R | Y | %
|  |  | 27268 | Min Voltage Unbalance C-N | 2 | FLOAT32 | R | Y | %
|  |  | 27270 | Min Voltage Unbalance L-N Worst | 2 | FLOAT32 | R | Y | %
Power
|  |  | 27272 | Min Active Power A | 2 | FLOAT32 | R | Y | kW
|  |  | 27274 | Min Active Power B | 2 | FLOAT32 | R | Y | kW
|  |  | 27276 | Min Active Power C | 2 | FLOAT32 | R | Y | kW
|  |  | 27278 | Min Active Power Total | 2 | FLOAT32 | R | Y | kW
|  |  | 27280 | Min Reactive Power A | 2 | FLOAT32 | R | Y | kVAR
|  |  | 27282 | Min Reactive Power B | 2 | FLOAT32 | R | Y | kVAR
|  |  | 27284 | Min Reactive Power C | 2 | FLOAT32 | R | Y | kVAR
|  |  | 27286 | Min Reactive Power Total | 2 | FLOAT32 | R | Y | kVAR
|  |  | 27288 | Min Apparent Power A | 2 | FLOAT32 | R | Y | kVA
|  |  | 27290 | Min Apparent Power B | 2 | FLOAT32 | R | Y | kVA
|  |  | 27292 | Min Apparent Power C | 2 | FLOAT32 | R | Y | kVA
|  |  | 27294 | Min Apparent Power Total | 2 | FLOAT32 | R | Y | kVA
Power Factor
|  |  | 27306 | Min Power Factor A | 2 | 4Q FP PF | R | Y | ---
|  |  | 27308 | Min Power Factor B | 2 | 4Q FP PF | R | Y | ---
|  |  | 27310 | Min Power Factor C | 2 | 4Q FP PF | R | Y | ---
|  |  | 27312 | Min Power Factor Total | 2 | 4Q FP PF | R | Y | ---
|  |  | 27314 | Min Displacement Power Factor A | 2 | 4Q FP PF | R | Y | ---
|  |  | 27316 | Min Displacement Power Factor B | 2 | 4Q FP PF | R | Y | ---
|  |  | 27318 | Min Displacement Power Factor C | 2 | 4Q FP PF | R | Y | ---
|  |  | 27320 | Min Displacement PF Total | 2 | 4Q FP PF | R | Y | ---
Total Harmonic Distortion, Current
|  |  | 27338 | Min THD Current A | 2 | FLOAT32 | R | Y | % | THD = (RMS of harmonics / RMS of fundamental) * 100
|  |  | 27340 | Min THD Current B | 2 | FLOAT32 | R | Y | %
|  |  | 27342 | Min THD Current C | 2 | FLOAT32 | R | Y | %
|  |  | 27344 | Min THD Current N | 2 | FLOAT32 | R | Y | %
|  |  | 27346 | Min THD Current G | 2 | FLOAT32 | R | Y | %
|  |  | 27348 | Min thd Current A | 2 | FLOAT32 | R | Y | % | thd = (RMS of harmonics / total RMS) * 100
|  |  | 27350 | Min thd Current B | 2 | FLOAT32 | R | Y | %
|  |  | 27352 | Min thd Current C | 2 | FLOAT32 | R | Y | %
|  |  | 27354 | Min thd Current N | 2 | FLOAT32 | R | Y | %
|  |  | 27356 | Min thd Current G | 2 | FLOAT32 | R | Y | %
Total Demand Distortion
|  |  | 27358 | Min Total Demand Distortion | 2 | FLOAT32 | R | Y | %
Total Harmonic Distortion, Voltage
|  |  | 27360 | Min THD Voltage A-B | 2 | FLOAT32 | R | Y | %
|  |  | 27362 | Min THD Voltage B-C | 2 | FLOAT32 | R | Y | %
|  |  | 27364 | Min THD Voltage C-A | 2 | FLOAT32 | R | Y | %
|  |  | 27366 | Min THD Voltage L-L Avg | 2 | FLOAT32 | R | Y | %
|  |  | 27368 | Min THD Voltage A-N | 2 | FLOAT32 | R | Y | %
|  |  | 27370 | Min THD Voltage B-N | 2 | FLOAT32 | R | Y | %
|  |  | 27372 | Min THD Voltage C-N | 2 | FLOAT32 | R | Y | %
|  |  | 27376 | Min THD Voltage L-N Avg | 2 | FLOAT32 | R | Y | %
|  |  | 27378 | Min thd Voltage A-B | 2 | FLOAT32 | R | Y | %
|  |  | 27380 | Min thd Voltage B-C | 2 | FLOAT32 | R | Y | %
|  |  | 27382 | Min thd Voltage C-A | 2 | FLOAT32 | R | Y | %
|  |  | 27384 | Min thd Voltage L-L Avg | 2 | FLOAT32 | R | Y | %
|  |  | 27386 | Min thd Voltage A-N | 2 | FLOAT32 | R | Y | %
|  |  | 27388 | Min thd Voltage B-N | 2 | FLOAT32 | R | Y | %
|  |  | 27390 | Min thd Voltage C-N | 2 | FLOAT32 | R | Y | %
|  |  | 27394 | Min thd Voltage L-N Avg | 2 | FLOAT32 | R | Y | %
Frequency
|  |  | 27616 | Min Frequency | 2 | FLOAT32 | R | Y | Hz
Maximum Values
Current
|  |  | 27694 | Max Current A | 2 | FLOAT32 | R | Y | A
|  |  | 27696 | Max Current B | 2 | FLOAT32 | R | Y | A
|  |  | 27698 | Max Current C | 2 | FLOAT32 | R | Y | A
|  |  | 27700 | Max Current N | 2 | FLOAT32 | R | Y | A
|  |  | 27702 | Max Current G | 2 | FLOAT32 | R | Y | A
|  |  | 27704 | Max Current Avg | 2 | FLOAT32 | R | Y | A
Current Unbalance
|  |  | 27706 | Max Current Unbalance A | 2 | FLOAT32 | R | Y | %
|  |  | 27708 | Max Current Unbalance B | 2 | FLOAT32 | R | Y | %
|  |  | 27710 | Max Current Unbalance C | 2 | FLOAT32 | R | Y | %
|  |  | 27712 | Max Current Unbalance Worst | 2 | FLOAT32 | R | Y | %
Voltage
|  |  | 27714 | Max Voltage A-B | 2 | FLOAT32 | R | Y | V
|  |  | 27716 | Max Voltage B-C | 2 | FLOAT32 | R | Y | V
|  |  | 27718 | Max Voltage C-A | 2 | FLOAT32 | R | Y | V
|  |  | 27720 | Max Voltage L-L Avg | 2 | FLOAT32 | R | Y | V
|  |  | 27722 | Max Voltage A-N | 2 | FLOAT32 | R | Y | V
|  |  | 27724 | Max Voltage B-N | 2 | FLOAT32 | R | Y | V
|  |  | 27726 | Max Voltage C-N | 2 | FLOAT32 | R | Y | V
|  |  | 27730 | Max Voltage L-N Avg | 2 | FLOAT32 | R | Y | V
Voltage Unbalance
|  |  | 27732 | Max Voltage Unbalance A-B | 2 | FLOAT32 | R | Y | %
|  |  | 27734 | Max Voltage Unbalance B-C | 2 | FLOAT32 | R | Y | %
|  |  | 27736 | Max Voltage Unbalance C-A | 2 | FLOAT32 | R | Y | %
|  |  | 27738 | Max Voltage Unbalance L-L Worst | 2 | FLOAT32 | R | Y | %
|  |  | 27740 | Max Voltage Unbalance A-N | 2 | FLOAT32 | R | Y | %
|  |  | 27742 | Max Voltage Unbalance B-N | 2 | FLOAT32 | R | Y | %
|  |  | 27744 | Max Voltage Unbalance C-N | 2 | FLOAT32 | R | Y | %
|  |  | 27746 | Max Voltage Unbalance L-N Worst | 2 | FLOAT32 | R | Y | %
Power
|  |  | 27748 | Max Active Power A | 2 | FLOAT32 | R | Y | kW
|  |  | 27750 | Max Active Power B | 2 | FLOAT32 | R | Y | kW
|  |  | 27752 | Max Active Power C | 2 | FLOAT32 | R | Y | kW
|  |  | 27754 | Max Active Power Total | 2 | FLOAT32 | R | Y | kW
|  |  | 27756 | Max Reactive Power A | 2 | FLOAT32 | R | Y | kVAR
|  |  | 27758 | Max Reactive Power B | 2 | FLOAT32 | R | Y | kVAR
|  |  | 27760 | Max Reactive Power C | 2 | FLOAT32 | R | Y | kVAR
|  |  | 27762 | Max Reactive Power Total | 2 | FLOAT32 | R | Y | kVAR
|  |  | 27764 | Max Apparent Power A | 2 | FLOAT32 | R | Y | kVA
|  |  | 27766 | Max Apparent Power B | 2 | FLOAT32 | R | Y | kVA
|  |  | 27768 | Max Apparent Power C | 2 | FLOAT32 | R | Y | kVA
|  |  | 27770 | Max Apparent Power Total | 2 | FLOAT32 | R | Y | kVA
Power Factor
|  |  | 27782 | Max Power Factor A | 2 | 4Q FP PF | R | Y | ---
|  |  | 27784 | Max Power Factor B | 2 | 4Q FP PF | R | Y | ---
|  |  | 27786 | Max Power Factor C | 2 | 4Q FP PF | R | Y | ---
|  |  | 27788 | Max Power Factor Total | 2 | 4Q FP PF | R | Y | ---
|  |  | 27790 | Max Displacement Power Factor A | 2 | 4Q FP PF | R | Y | ---
|  |  | 27792 | Max Displacement Power Factor B | 2 | 4Q FP PF | R | Y | ---
|  |  | 27794 | Max Displacement Power Factor C | 2 | 4Q FP PF | R | Y | ---
|  |  | 27796 | Max Displacement PF Total | 2 | 4Q FP PF | R | Y | ---
Total Harmonic Distortion, Current
|  |  | 27814 | Max THD Current A | 2 | FLOAT32 | R | Y | % | THD = (RMS of harmonics / RMS of fundamental) * 100
|  |  | 27816 | Max THD Current B | 2 | FLOAT32 | R | Y | %
|  |  | 27818 | Max THD Current C | 2 | FLOAT32 | R | Y | %
|  |  | 27820 | Max THD Current N | 2 | FLOAT32 | R | Y | %
|  |  | 27822 | Max THD Current G | 2 | FLOAT32 | R | Y | %
|  |  | 27824 | Max thd Current A | 2 | FLOAT32 | R | Y | % | thd = (RMS of harmonics / total RMS) * 100
|  |  | 27826 | Max thd Current B | 2 | FLOAT32 | R | Y | %
|  |  | 27828 | Max thd Current C | 2 | FLOAT32 | R | Y | %
|  |  | 27830 | Max thd Current N | 2 | FLOAT32 | R | Y | %
|  |  | 27832 | Max thd Current G | 2 | FLOAT32 | R | Y | %
Total Demand Distortion
|  |  | 27834 | Max Total Demand Distortion | 2 | FLOAT32 | R | Y | %
Total Harmonic Distortion, Voltage
|  |  | 27836 | Max THD Voltage A-B | 2 | FLOAT32 | R | Y | %
|  |  | 27838 | Max THD Voltage B-C | 2 | FLOAT32 | R | Y | %
|  |  | 27840 | Max THD Voltage C-A | 2 | FLOAT32 | R | Y | %
|  |  | 27842 | Max THD Voltage L-L | 2 | FLOAT32 | R | Y | %
|  |  | 27844 | Max THD Voltage A-N | 2 | FLOAT32 | R | Y | %
|  |  | 27846 | Max THD Voltage B-N | 2 | FLOAT32 | R | Y | %
|  |  | 27848 | Max THD Voltage C-N | 2 | FLOAT32 | R | Y | %
|  |  | 27852 | Max THD Voltage L-N | 2 | FLOAT32 | R | Y | %
|  |  | 27854 | Max thd Voltage A-B | 2 | FLOAT32 | R | Y | %
|  |  | 27856 | Max thd Voltage B-C | 2 | FLOAT32 | R | Y | %
|  |  | 27858 | Max thd Voltage C-A | 2 | FLOAT32 | R | Y | %
|  |  | 27860 | Max thd Voltage L-L | 2 | FLOAT32 | R | Y | %
|  |  | 27862 | Max thd Voltage A-N | 2 | FLOAT32 | R | Y | %
|  |  | 27864 | Max thd Voltage B-N | 2 | FLOAT32 | R | Y | %
|  |  | 27866 | Max thd Voltage C-N | 2 | FLOAT32 | R | Y | %
|  |  | 27870 | Max thd Voltage L-N | 2 | FLOAT32 | R | Y | %
Frequency
|  |  | 28092 | Max Frequency | 2 | FLOAT32 | R | Y | Hz