## SIEMENS SENTRON PAC 4200
MODBUS offset | Description | Units | Data type
1 | Voltage a-n | V | single
3 | Voltage b-n | V | single
5 | Voltage c-n | V | single
7 | Voltage a-b | V | single
9 | Voltage b-c | V | single
11 | Voltage c-a | V | single
13 | Current a | A | single
15 | Current b | A | single
17 | Current c | A | single
19 | Apparent Power a | V | single
21 | Apparent Power b | V | single
23 | Apparent Power c | V | single
25 | Active Power a | W | single
27 | Active Power b | W | single
29 | Active Power c | W | single
31 | Reactive Power a (VARn) | V | single
33 | Reactive Power b (VARn) | V | single
35 | Reactive Power c (VARn) | V | single
37 | Power Factor a | - | single
39 | Power Factor b | - | single
41 | Power Factor c | - | single
43 | THD Voltage a-b | % | single
45 | THD Voltage b-c | % | single
47 | THD Voltage c-a | % | single
55 | Line Frequency | H | single
57 | 3-Phase Average Voltage ph-n | V | single
59 | 3-Phase Average Voltage ph-ph | V | single
61 | 3-Phase Average Current ph-ph | A | single
63 | Total Apparent Power | V | single
65 | Total Active Power | W | single
67 | Total Reactive Power (VARn) | V | single
69 | Total Power Factor | - | single
71 | Amplitude Unbalance Voltage | % | single
73 | Amplitude Unbalance Current | % | single
75 | Maximum Voltage a-n | V | single
77 | Maximum Voltage b-n | V | single
79 | Maximum Voltage c-n | V | single
81 | Maximum Voltage a-b | V | single
83 | Maximum Voltage b-c | V | single
85 | Maximum Voltage c-a | V | single
87 | Maximum Current a | A | single
89 | Maximum Current b | A | single
91 | Maximum Current c | A | single
93 | Maximum Apparent Power a | V | single
95 | Maximum Apparent Power b | V | single
97 | Maximum Apparent Power c | V | single
99 | Maximum Active Power a | W | single
101 | Maximum Active Power b | W | single
103 | Maximum Active Power c | W | single
105 | Maximum Reactive Power a (VARn) | V | single
107 | Maximum Reactive Power b (VARn) | V | single
109 | Maximum Reactive Power c (VARn) | V | single
111 | Maximum Power Factor a | - | single
113 | Maximum Power Factor b | - | single
115 | Maximum Power Factor c | - | single
117 | Maximum THD Voltage a-b | % | single
119 | Maximum THD Voltage b-c | % | single
121 | Maximum THD Voltage c-a | % | single
129 | Maximum Line Frequency | H | single
131 | Maximum 3-Phase Average Voltage | V | single
133 | Maximum 3-Phase Average Voltage | V | single
135 | Maximum 3-Phase Average Current | A | single
137 | Maximum Total Apparent Power | V | single
139 | Maximum Total Active Power | W | single
141 | Maximum Total Reactive Power | V | single
143 | Maximum Total Power Factor | - | single
145 | Minimum Voltage a-n | V | single
147 | Minimum Voltage b-n | V | single
149 | Minimum Voltage c-n | V | single
151 | Minimum Voltage a-b | V | single
153 | Minimum Voltage b-c | V | single
155 | Minimum Voltage c-a | V | single
157 | Minimum Current a | A | single
159 | Minimum Current b | A | single
161 | Minimum Current c | A | single
163 | Minimum Apparent Power a | V | single
165 | Minimum Apparent Power b | V | single
167 | Minimum Apparent Power c | V | single
169 | Minimum Active Power a | W | single
171 | Minimum Active Power b | W | single
173 | Minimum Active Power c | W | single
175 | Minimum Reactive Power a (VARn) | V | single
177 | Minimum Reactive Power b (VARn) | V | single
179 | Minimum Reactive Power c (VARn) | V | single
181 | Minimum Power Factor a | - | single
183 | Minimum Power Factor b | - | single
185 | Minimum Power Factor c | - | single
187 | Minimum Line Frequency | H | single
189 | Minimum 3-Phase Average Voltage | V | single
191 | Minimum 3-Phase Average Voltage | V | single
193 | Minimum 3-Phase Average Current | A | single
195 | Minimum Total Apparent Power | V | single
197 | Minimum Total Active Power | W | single
199 | Minimum Total Reactive Power (VARn) | V | single
201 | Minimum Total Power Factor | V | single
203 | Limit Violations* | - | cardinal
205 | PMD Diagnostics and Status* | - | cardinal
207 | Digital Outputs* Status | - | cardinal
209 | Digital Inputs* Status | - | cardinal
211 | Active Tariff | - | cardinal
213 | Operating Hours Counter**) | s | cardinal
215 | Universal Counter**) | - | cardinal
217 | Relevant Parameter Changes Counter | - | cardinal
219 | Counter All Parameter Changes | - | cardinal
221 | Counter Limit Violations | - | cardinal
223 | Event Counter | - | cardinal
225 | Alarm Counter | - | cardinal
227 | Load Profile Counter | - | cardinal
229 | Misc. Counter | - | cardinal
231 | Status Digital Outputs Module 1 | - | cardinal
233 | Status Digital Inputs Module 1 | - | cardinal
235 | Status Digital Outputs Module 2 | - | cardinal
237 | Status Digital Inputs Module 2 | - | cardinal
243 | Cos F a | - | single
245 | Cos F b | - | single
247 | Cos F c | - | single
249 | Displacement Angle a | Degree | single
251 | Displacement Angle b | Degree | single
253 | Displacement Angle c | Degree | single
255 | Phase Angle a-a | Degree | single
257 | Phase Angle a-b | Degree | single
259 | Phase Angle a-c | Degree | single
261 | THD Voltage a | % | single
263 | THD Voltage b | % | single
265 | THD Voltage c | % | single
267 | THD Current a | % | single
269 | THD Current b | % | single
271 | THD Current c | % | single
273 | Distortion Current a | A | single
275 | Distortion Current b | A | single
277 | Distortion Current c | A | single
279 | Total Reactive Power a (VARtot) | V | single
281 | Total Reactive Power b (VARtot) | V | single
283 | Total Reactive Power c (VARtot) | V | single
285 | Reactive Power a (VAR1) | V | single
287 | Reactive Power a (VAR1) | V | single
289 | Reactive Power a (VAR1) | V | single
291 | Unbalance Voltage | % | single
293 | Unbalance Current | % | single
295 | Neutral Current | A | single
297 | Total Reactive Power (VARtot) | V | single
299 | Total Reactive Power (VAR1) | V | single
301 | Sliding Window Demand Voltage a-n | V | single
303 | Sliding Window Demand Voltage b-n | V | single
305 | Sliding Window Demand Voltage c-n | V | single
307 | Sliding Window Demand Voltage a-b | V | single
309 | Sliding Window Demand Voltage b-c | V | single
311 | Sliding Window Demand Voltage c-a | V | single
313 | Sliding Window Demand Current a | A | single
315 | Sliding Window Demand Current b | A | single
317 | Sliding Window Demand Current c | A | single
319 | Sliding Window Demand Apparent | V | single
321 | Sliding Window Demand Apparent | V | single
323 | Sliding Window Demand Apparent | V | single
325 | Sliding Window Demand Active Power | W | single
327 | Sliding Window Demand Active Power | W | single
329 | Sliding Window Demand Active Power | W | single
331 | Sliding Window Demand Reactive | V | single
333 | Sliding Window Demand Reactive | V | single
335 | Sliding Window Demand Reactive | V | single
337 | Sliding Window Demand Total | V | single
339 | Sliding Window Demand Total | V | single
341 | Sliding Window Demand Total | V | single
343 | Sliding Window Demand Reactive | V | single
345 | Sliding Window Demand Reactive | V | single
347 | Sliding Window Demand Reactive | V | single
349 | Sliding Window Demand Power Factor | - | single
351 | Sliding Window Demand Power Factor | - | single
353 | Sliding Window Demand Power Factor | - | single
355 | Sliding Window Demand Total | V | single
357 | Sliding Window Demand Total Active | W | single
359 | Sliding Window Demand Total | V | single
361 | Sliding Window Demand Total | V | single
363 | Sliding Window Demand Total | V | single
365 | Sliding Window Demand Total Power | - | single
367 | Sliding Window Demand Neutral | A | single

## SIEMENS SENTRON PAC 3200
MODBUS offset | Description | Units | Data type
1 | Voltage Va-n | V | single
3 | Voltage Vb-n | V | single
5 | Voltage Vc-n | V | single
7 | Voltage Va-b | V | single
9 | Voltage Vb-c | V | single
11 | Voltage Vc-a | V | single
13 | Current a | A | single
15 | Current b | A | single
17 | Current c | A | single
19 | Apparent Power a | V | single
21 | Apparent Power b | V | single
23 | Apparent Power c | V | single
25 | Active Power a | W | single
27 | Active Power b | W | single
29 | Active Power c | W | single
31 | Reactive Power a | v | single
33 | Reactive Power b | v | single
35 | Reactive Power c | v | single
37 | Power Factor a | - | single
39 | Power Factor b | - | single
41 | Power Factor c | - | single
43 | THD-R Voltage a | % | single
45 | THD-R Voltage b | % | single
47 | THD-R Voltage c | % | single
49 | THD-R Current a | % | single
51 | THD-R Current b | % | single
53 | THD-R Current c | % | single
55 | Frequency | H | single
57 | Average Voltage Vph-n | V | single
59 | Average Voltage Vph-ph | V | single
61 | Average Current | A | single
63 | Total Apparent Power | V | single
65 | Total Active Power | W | single
67 | Total Reactive Power | v | single
69 | Total Power Factor | - | single
71 | Amplitude Unbalance - Voltage | % | single
73 | Amplitude Unbalance - Current | % | single
75 | Maximum Voltage Va-n | V | single
77 | Maximum Voltage Vb-n | V | single
79 | Maximum Voltage Vc-n | V | single
81 | Max. Voltage Va-b | V | single
83 | Max. Voltage Vb-c | V | single
85 | Max. Voltage Vc-a | V | single
87 | Maximum Current a | A | single
89 | Maximum Current b | A | single
91 | Maximum Current c | A | single
93 | Maximum Apparent Power a | V | single
95 | Maximum Apparent Power b | V | single
97 | Maximum Apparent Power c | V | single
99 | Maximum Active Power a | W | single
101 | Maximum Active Power b | W | single
103 | Maximum Active Power c | W | single
105 | Maximum Reactive Power a | v | single
107 | Maximum Reactive Power b | v | single
109 | Maximum Reactive Power c | v | single
111 | Maximum Power Factor a |  | single
113 | Maximum Power Factor b |  | single
115 | Maximum Power Factor c |  | single
117 | Maximum THD-R Voltage a | % | single
119 | Maximum THD-R Voltage b | % | single
121 | Maximum THD-R Voltage c | % | single
123 | Maximum THD-R Current a | % | single
125 | Maximum THD-R Current b | % | single
127 | Maximum THD-R Current c | % | single
129 | Max. Frequency | H | single
131 | Max. Average Voltage Vph-n | V | single
133 | Max. Average Voltage Vph-ph | V | single
135 | Max. Average Current | A | single
137 | Max. Total Apparent Power | V | single
139 | Max. Total Active Power | W | single
141 | Max. Total Reactive Power | v | single
143 | Maximum Total Power Factor | - | single
145 | Minimum Voltage Va-n | V | single
147 | Minimum Voltage Vb-n | V | single
149 | Minimum Voltage Vc-n | V | single
151 | Min. Voltage Va-b | V | single
153 | Min. Voltage Vb-c | V | single
155 | Min. Voltage Vc-a | V | single
157 | Minimum Current a | A | single
159 | Minimum Current b | A | single
161 | Minimum Current c | A | single
163 | Minimum Apparent Power a | V | single
165 | Minimum Apparent Power b | V | single
167 | Minimum Apparent Power c | V | single
169 | Minimum Active Power a | W | single
171 | Minimum Active Power b | W | single
173 | Minimum Active Power c | W | single
175 | Minimum Reactive Power a | v | single
177 | Minimum Reactive Power b | v | single
179 | Minimum Reactive Power c | v | single
181 | Minimum Power Factor a | - | single
183 | Minimum Power Factor b | - | single
185 | Minimum Power Factor c | - | single
187 | Min. Frequency | H | single
189 | Min. Average Voltage Vph-n | V | single
191 | Min. Average Voltage Vph-ph | V | single
193 | Min. Average Current | A | single
195 | Min. Total Apparent Power | V | single
197 | Min. Total Active Power | W | single
199 | Min. Total Reactive Power | v | single
201 | Minimum Total Power Factor | v | single
203 | Limit Violations* | - | cardinal
205 | Device Diagnostics and Device Status* | - | cardinal
207 | Status of the Digital Outputs | - | cardinal
209 | Status of the Digital Inputs | - | cardinal
211 | Active Tariff | - | cardinal
213 | Working hours counter | s | cardinal
215 | Universal counter | - | cardinal
217 | Relevant Parameter Changes Counter | - | cardinal
219 | Counter All Parameter Changes | - | cardinal
501 | Demand Active Power - Import | W | single
503 | Demand Reactive Power - Import | v | single
505 | Demand Active Power - Export | W | single
507 | Demand Reactive Power - Export | v | single
509 | Maximum Active Power Reading during the period | W | single
511 | Minimum Active Power Reading during the period | W | single
513 | Maximum Reactive Power Reading during the period | v | single
515 | Minimum Reactive Power Reading during the period | v | single
517 | Demand Period | s | cardinal
519 | Time Since Start of the active demand period | s | cardinal
801 | Active Energy Import Tariff 1 | W | double
805 | Active Energy Import Tariff 2 | W | double
809 | Active Energy Export Tariff 1 | W | double
813 | Active Energy Export Tariff 2 | W | double
817 | Reactive Energy Import Tariff 1 | v | double
821 | Reactive Energy Import Tariff 2 | v | double
825 | Reactive Energy Export Tariff 1 | v | double
829 | Reactive Energy Export Tariff 2 | v | double
833 | Apparent Energy Tariff 1 | V | double
837 | Apparent Energy Tariff 2 | V | double

## Sheet1
559814B5-D28C-42F9-B8BD-5A8CKSS1111 | R-Phase to Neutral Voltage | R-Phase to Neutral Voltage | V1 | 30002 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 1 | FALSE | FALSE | 37 | V | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 807b5e83-8baf-406f-99d1-03cdab9a2efb
559814B5-D28C-42F9-B8BD-5A8CKSS1112 | Y-Phase to Neutral Voltage | Y-Phase to Neutral Voltage | V2 | 30004 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 2 | FALSE | FALSE | 37 | V | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 3008d6d0-a363-4574-b36b-1fa0e496d26a
559814B5-D28C-42F9-B8BD-5A8CKSS1113 | B-Phase to Neutral Voltage | B-Phase to Neutral Voltage | V3 | 30006 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 3 | FALSE | FALSE | 37 | V | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | d2fa3af7-3407-40f8-b58c-c1b6b5466193
559814B5-D28C-42F9-B8BD-5A8CKSS1114 | R-Y Phase Voltage | R-Y Phase Voltage | RYV | 30008 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 1 | FALSE | FALSE | 37 | V | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 807b5e83-8baf-406f-99d1-03cdab9a2efb
559814B5-D28C-42F9-B8BD-5A8CKSS1115 | Y-B Phase Voltage | Y-B Phase Voltage | YBV | 30010 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 2 | FALSE | FALSE | 37 | V | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 3008d6d0-a363-4574-b36b-1fa0e496d26a
559814B5-D28C-42F9-B8BD-5A8CKSS1116 | B-R Phase Voltage | B-R Phase Voltage | BRV | 30012 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 3 | FALSE | FALSE | 37 | V | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | d2fa3af7-3407-40f8-b58c-c1b6b5466193
559814B5-D28C-42F9-B8BD-5A8CKSS1117 | R-Phase Current | R-Phase Current | I1 | 30014 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 4 | FALSE | TRUE | 37 | A | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 3751da28-80c1-45b7-bcc4-db9621b204c0
559814B5-D28C-42F9-B8BD-5A8CKSS1118 | Y-Phase Current | Y-Phase Current | I2 | 30016 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 5 | FALSE | TRUE | 37 | A | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 34f73a64-cf9f-4b4a-9a35-cf8ef0e841af
559814B5-D28C-42F9-B8BD-5A8CKSS1119 | B-Phase Current | B-Phase Current | I3 | 30018 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 6 | FALSE | TRUE | 37 | A | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 27cfa92c-3a6a-45f8-b29b-226eead5337d
559814B5-D28C-42F9-B8BD-5A8CKSS1120 | R-Phase Apparent Power | R-Phase Apparent Power | RKVA | 30020 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 7 | FALSE | FALSE | 37 | KVA | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 5efc7a3a-d5e6-4e07-88ea-b1082ab2f4e4
559814B5-D28C-42F9-B8BD-5A8CKSS1121 | Y-Phase Apparent Power | Y-Phase Apparent Power | YKVA | 30022 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 8 | FALSE | FALSE | 37 | KVA | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 7da91c3a-ba7a-491f-9ac5-26b22e4324d2
559814B5-D28C-42F9-B8BD-5A8CKSS1122 | B-Phase Apparent Power | B-Phase Apparent Power | BKVA | 30024 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 9 | FALSE | FALSE | 37 | KVA | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 82270edd-81f2-4e7c-bad6-ae7725c7fa89
559814B5-D28C-42F9-B8BD-5A8CKSS1123 | R-Phase Active Power | R-Phase Active Power | RKW | 30026 | 0.001 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 7 | FALSE | FALSE | 37 | KW | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 5efc7a3a-d5e6-4e07-88ea-b1082ab2f4e4
559814B5-D28C-42F9-B8BD-5A8CKSS1124 | Y-Phase Active Power | Y-Phase Active Power | YKW | 30028 | 0.001 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 8 | FALSE | FALSE | 37 | KW | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 7da91c3a-ba7a-491f-9ac5-26b22e4324d2
559814B5-D28C-42F9-B8BD-5A8CKSS1125 | B-Phase Active Power | B-Phase Active Power | BKW | 30030 | 0.001 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 9 | FALSE | FALSE | 37 | KW | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 82270edd-81f2-4e7c-bad6-ae7725c7fa89
559814B5-D28C-42F9-B8BD-5A8CKSS1126 | Frequency | Frequency | F | 30056 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 14 | TRUE | FALSE | 37 | Hz | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 | NULL | NULL | NULL | S | 43521.5734 | db2c0cd7-0d4c-4416-8874-fadca16282ca
559814B5-D28C-42F9-B8BD-5A8CKSS1127 | Line to Line Avg Voltage | Line to Line Avg Voltage | LLV | 30058 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 11 | FALSE | TRUE | 37 | V | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 | NULL | NULL | NULL | S | 42801.5183 | 53614529-535c-40d5-9bd7-1c121394642a
559814B5-D28C-42F9-B8BD-5A8CKSS1128 | Line to Neutral Voltage | Line to Neutral Voltage | LNV | 30060 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 12 | FALSE | TRUE | 37 | V | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 | NULL | NULL | NULL | S | 42801.5183 | e14cbc25-79cf-4dd4-a06d-edb34e434613
559814B5-D28C-42F9-B8BD-5A8CKSS1129 | Average Current | Average Current | AvgI | 30062 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 13 | FALSE | TRUE | 37 | A | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 | NULL | NULL | NULL | S | 42801.5183 | f762f823-1329-4dc9-97f8-61b45b7d2b0e
559814B5-D28C-42F9-B8BD-5A8CKSS1130 | Apparent Power-Avg | Apparent Power-Avg | KVA | 30064 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 7 | FALSE | TRUE | 37 | KVA | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 | NULL | NULL | NULL | S | 42801.5183 | 3bdb6f31-b08a-4e20-849a-ea9a60967eb2
559814B5-D28C-42F9-B8BD-5A8CKSS1131 | Active Power-Avg | Active Power-Avg | KW | 30066 | 0.001 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 10 | FALSE | TRUE | 37 | KW | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | S | 43521.5667 | 4a3317ad-adae-4204-8857-64aa8a8746ee
559814B5-D28C-42F9-B8BD-5A8CKSS1132 | Reactive Power-Avg | Reactive Power-Avg | KVAR | 30068 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 9 | FALSE | TRUE | 37 | KVAR | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 | NULL | NULL | NULL | S | 42801.5183 | d418495f-038a-44b5-a73f-e5f81a9255d0
559814B5-D28C-42F9-B8BD-5A8CKSS1133 | Avg Power Factor | Avg Power Factor | PF | 30070 | 1 | Float 4321 | 2 | IO | Analog | 0 | 3 | M | 11 | TRUE | TRUE | 37 | PF | NULL | FALSE | TRUE | FALSE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | S | 43521.5667 | eb6d9e9d-b939-423a-a02d-3c1755873970
559814B5-D28C-42F9-B8BD-5A8CKSS1134 | Active Energy-Import | Active Energy-Import | KWHIm | 30802 | 0.001 | Double 87654321 | 4 | IO | Reading | 0 | 3 | M | 12 | FALSE | TRUE | 37 | KWH | NULL | TRUE | TRUE | TRUE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | U | 43521.5667 | 9c5e8b42-a18a-4199-a702-1fce8825efec
559814B5-D28C-42F9-B8BD-5A8CKSS1135 | Active Energy-Export | Active Energy-Export | KWHEx | 30810 | 0.001 | Double 87654321 | 4 | IO | Reading | 0 | 3 | M | 13 | FALSE | FALSE | 37 | KWH | NULL | TRUE | FALSE | TRUE | NULL | NULL | NULL | NULL | 0 | 0 | daa1800f-a4ed-4644-9af9-e858451895a2 |  |  |  | S | 43521.5667 | 07944f86-67cd-4309-9768-2cda6d283df5